## Chapter 1  Overview

This user’s manual describes the standard of positioning module, installation method, the method to use each positioning function, programming and the wiring with external machine as below.

| No. of Control Axis | Product Name |  | Related S/W Package |
| --- | --- | --- | --- |
|  | Open Collector | Line Drive |  |
| 1 Axis | G4F-PP1O G6F-PP1O | G4F-PP1D G6F-PP1D | APM S/W Package |
| 2 Axis | G4F-PP2O G6F-PP2O | G4F-PP2D G6F-PP2D |  |
| 3 Axis | G4F-PP3O G6F-PP3O | G4F-PP3D G6F-PP3D |  |

G4F-PP1O,G4F-PP2O,G4F-PP3O,G4F-PP1D,G4F-PP2D,G4F-PP3D,G6F-PP1O,G6F-PP2O,G6F-PP3O,

G6F-PP1D,G6F-PP2D,G6F-PP3D modules are described APM(advanced position module).

1.1 Characteristics

The features of positioning module is as follows :

- The positioning module is available for GLOFA GM Series and MASTER-K Series.

- Various positioning control function

It has various functions needed for positioning system such as positioning control at the random position, equal speed operation etc.

- The operation data including positioning address and operation method, operation pattern is available to set max. 400 at each axis.

With this operation data, the positioning at each axis is carried out.

(2/3 axis interpolation control and 2/3 axis simultaneous setting is available.)

- In case of positioning at each axis, the straight line control (3 axis simultaneous setting available) is available.

This control enables the single position control by one operation data and the continuous position control by plural operation data.

- In case of positioning more than 2 axis, speed control, interpolation control and circular arcs interpolation control of 2 axis are available.

- According to the control method designated by each operation data and parameter, there are position control, speed control, speed/position switching control, position/speed switching control.

- Abundant origin return control function.

(A) The method of origin return is shown as below and available to select one from 5 methods.

▶The origin detection after approximate origin OFF

▶The origin detection after deceleration in case of approximate origin ON

▶The origin detection by the origin and high-low limit

▶The origin detection by approximate origin

▶High speed origin detection

(B) Available to execute the positioning control (floating origin setting) from random position to the origin of machine.

- The Acceleration/Deceleration method contains trapezoid and S-type to select.

- High speeding of setting process

Due to the realization of high speeding of positioning operation setting process, the setting process time reduced by  4ms~ 5ms.

Therefore, the delay time will not occur between axis in case of simultaneous setting (using several axis or during interpolation operation).

- High speeding of pulse output and making a long-distance connection with driver

In case of using Line Drive type (G4F-PP1D, G4F-PP2D, G4F-PP3D, G6F-PP1D, G6F-PP2D, G6F-PP3D), it is available to realize the high speeding and making a long-distance connection.

- Simplicity of maintenance

Various data such as positioning data, parameter etc. is saved in flash memory within positioning module.

- The number of positioning module using in one base is not limited.
(but available to use within the range that satisfies the capacity of power module)

- Self-diagnosis, monitoring, test by strong positioning software package is available.

  - Diagnosis for I/O signal line

  - Monitoring

  - Tracking

  - Simulation

  - Detailed information and solution for each error is provided.

  - Printer function in various ways is provided.

  - Operation data editing of each axis is available in Excel program.

1.2 Purpose of Positioning Control

The purpose of positioning module is to transfer the moving objects (unprocessed items, tools etc.) by setting speed from the current position and stop them on the setting position correctly. And it also control the position of high precision by positioning pulse string signal as it is connected to various servo running devices or stepping motor control running devices.

In application, it can be used widely with engineering machine, semiconductor assembly machine, grinder, small machine center, lifter etc.

CPU Module

Positioning Module

Program

Setting

Data

Polyphase Pulse Generator

Pulse AMP

Stepping Motor

M

Driver

Read, Write

Normal Rotation Pulse

Reverse Rotation Pulse

CPU Module

Positioning Module

Program

Setting

Data

Deviation

Counter

D/A

Converter

Speed Order

SERVO

AMP

SERVO Motor

Interface

APM

Software Package

Driver

Read, Write

Normal Rotation Pulse

Reverse Rotation Pulse

Feedback Pulse

Speed

Time

SERVO Motor Speed

Pulse Amount

Accumulative Pulse

APM

Software Package

[Fig. 1-1]  Overview of Position Control for Stepping Motor

M

PG

[Fig. 1-2] Overview of Position Control for SERVO Motor

1.3 Signal Flow of Positioning Module

The flow of PLC system using the positioning module is as follows :

.

PLC

CPU Module

Program Writing

GMWIN

KGLWIN

APM

Software Package

Setting of Parameter

and Operation Data

for Control

Test operation

- Jog operation

- Inching operation

- Indirect setting

- Direct setting

- Synchronous setting

- Straight line

interpolation operation

- Circular arcs

interpolation operation

- Position synchronization

operation

- Speed synchronization

operation

Monitoring and test of

positioning action,

using the setting command

Positioning Module

External setting signal

Emergency stop signal

Stop signal

Jog operation signal

Skip operation signal

External simultaneous

setting signal

Speed/position switching

signal–To positioning

module

External Signal

MPG

Encoder

Motor

SERVO

AMP

Working

Setting by external

pulse string

Action by SERVO

indication

Motor Driving by pulse

string received from

positioning module

Transfer Drive Ready

signal and Home signal

to positioning module

- When using GM4 CPUA,B module, ROM version should be more than V2.6 and GMWIN V3.6.

- When using K300S CPUA module, ROM version should be more than V3.1 and KGL-WIN V3.3.

- When using GM6 CPUA,B,C module, ROM version should be more than V2.0 and GMWIN V3.63

- When using K200S CPUA,B,C module, ROM version should be more than V2.3 and KGL-WIN V3.3.

Point