# Chapter 12 Operation Order and Installation

12.1 Operation Order

▶Here describes the Operation order in case of positioning operation by positioning

Start

Fix positioning operation method and control unit

Install positioning software package to computer.

Positioning data preparation by software package

▶Positioning parameter (X, Y, Z axis)

▶Operation data (X, Y, Z axis)

Install positioning module to the base.

Positioning module,drive machine,motor, connection between external machine

Drive Unit Ready signal, high/low limit signal, emergency stop signal should be ON in wiring.

Power application to PLC system.

Positioning module system test

Setting data write by positioning module on PC

Positioning startup and various data setting/ change/monitoring

▶Origin address setting

▶positioning data setting (address) by teaching function, jog operation, manual pulse generator.

Positioning program write

Positioning operation by CPU module & positioning module

End

Fix the homing method, coordinate, operation mode, control unit for positioning operation.

Prepared by software package.

Power application when CPU module is “STOP”.

Wiring status check by positioning module LED indicator or software package

Operated by software package startup mode.

Check if positioning parameter, position data, speed data setting value is correct and save them by changing if necessary.

Written by software package

GMWIN or KGL-WIN

Select pulse output type of positioning module.

Select one from Open Collector and Line Driver.

Cable connection between Computer and RS-232c port of CPU

12.2 Installation

- 12.2.1 Installation Environment

This machine has a good reliability regardless of installation environment but cares should be taken in the following items to guarantee the reliability and safety of the system.

1) Environment Condition

- Install the control panel available for water-proof, anti-vibration.

- The place free from continuous impact or vibration.

- The place not exposed to direct rays.

- The place with no dew phenomena by rapid temperature change.

- The place where surrounding temperature maintains 0-55℃.

2) Installation Construction

- In case of processing the screw hole or wiring, cares should be taken not to put the wiring remnants to PLC inside.

- Install on the good place to operate.

- Do not install the high voltage machine on the same Panel.

- The distance from duct or surrounding module shall be more than 50mm.

- Ground to the place where surrounding noise environment is good enough.

- 12.2.2 Notices in Handling

Here describes the notices in handling the positioning module from opening to installation.

1) Do not fall down or apply the strong impact.

2) Do not remove PCB from the case. It may cause the failure.

3) In wiring, cares should be taken not to put the wiring remnants or foreign materials to the upper part of module. If something entered, it should be removed.

4) The removal of module in the status of power ON, is prohibited.

12.3 Wiring

- 12.3.1 Notices in Wiring

- The length of connecting cable between positioning module and drive machine shall be as short as possible. (Max. length : 2m).

- For cross current and external I/O signal of positioning module, it is required to use the separate cables to avoid the surge or induction noise generated from the cross current.

- The wires should be selected considering surrounding temperature, allowable current and it is recommended to be more than max.size AWG22(0.3㎟).

- In wiring, if it is too close to the high temperature machine or material or it is directly contacted to the oil for a long time, the short-circuit will occur that may cause the damage or malfunction.

- Make sure to check the polarity before applying the external contact signal to the terminal board.

- In case of wiring the high voltage cable and power cables together, the induction obstacle occurs that may cause the malfunction or failure.

- In case of wiring by the pipe, the grounding of pipe is required.

- For the power supplied from outside (DC 5V, DC24V), it is required to use the safe and stable power.

9)In case that there is considered to be the noise source in wiring between positioning module and drive machine, it is required to use and connect Twist pair and sealed cable for the wiring of output pulse that comes from the positioning and enters into the motor driver

12.3.2 Connection Example of Servo and Stepping Motor Drive Machine

1) MR-H□A Connection (Line drive)

R

S

T

R1

S1

N

C

P

U

V

W

U

V

W

E

P15R

1

36

49

11

35

11

12

15

13

40

46

22

37

17

39

20

9

8

23

48

21

38

10

SG

SG

EMG

SON

RES

TL

LSP

LSN

VIS

VDD

CR

SG

PP

PPR

NP

NPR

RD

LZ

LZR

VDD

ZSP

ALM

LG

N15R

TLAN

LG

SD

28

26

27

30

50

29

TLAP

4

3

1

MO1

MO2

MOG

G4F-PP1/2/3D

CN3

CN2

Power

3상 AC200V

MR-HA

VTP switching

DC24V

High limit

Low limit

External stop

Approx. origin

External comm.  comm..

Jog reverse

5V

A

B

0V

MPG

DC24V

Emergency stop

DRVIN

34

DRVIN COM

33

HOME COM

HOME +5V

38

RP-

RP+

24

21

FP+

22

FP-

23

37

25

OV-

STOP

OV+

28

DOG

29

VTP

30

ECMD

26

27

COM

JOG-

32

31

1

MPG A+

2

MPG A-

3

MPG B+

4

MPG B-

7

CON

COM

EMG

10

8

ZONE COM

ZONE 3

14

11

ZONE 1

12

ZONE 2

13

External EMG

Servo ON

Reset

Torque limit

Normal limit

Reverse limit

RA1

RA2

failure

Analog torque limit command (+)

+10V/max. current

Analog torque limit command(-)

-10V/max. current

Within 2m

Within 10m

Servo Motor

SM

Detector

Within 50m

Within 2m

Monitor output    10K

Revival         l

CN1

option

Zero speed detection

External simultaneous start

2) MR-J2/J2S-□A Connection (Line drive)

(1) G4F-PP1/2/3D

Within 10m

External EMG

Servo ON

Reset

Proportional control

Torque limit

Normal limit

Reverse limit

*3

*3

failure

zero speed detection

in torque limit

RA1

RA2

RA3

Analog torque limit

+10V/max. current

Power

3phase 200VAC

NF

RD

SD

GND

GND

RS

CS

DR

ER

L1

L2

L3

L11

L21

CTE2

D

P

CN1A

OPC

11

PP

3

PG

13

NP

2

NG

12

RD

19

COM

9

CR

8

SG

10

LZ

5

LZR

15

LG

1

SD

Plate

EMG

15

SON

5

RES

14

PC

8

TL

9

LSP

16

LSN

17

SG

10

SG

20

VDD

3

COM

13

ALM

18

ZSP

19

TLC

6

P15R

11

TLA

12

LG

1

SD

Plate

CN1E

TE11

MR-J2S-A

U

V

W

PE

PE

HC-MF HA-FF

Series motor

U

V

W

E

EMG

24VDC

CN2

B1

B2

SM

electronic brake

detector

2

1

12

TxD

RxD

LG

11

5

15

LG

LG

LG

4

3

14

13

Plate

GND

RS

CS

DR

ER

CN3

A

A

Monitor output

Max. 10mA

10k

10k

Personal

computer

Within 2m

Within 2m

MC

DRVIN

34

DRVIN COM

33

RP-

RP+

24

21

FP+

22

FP-

23

COM

32

25

OV-

STOP

OV+

28

DOG

29

VTP

30

ECMD

26

27

JOG-

31

VTP switching

DC24V

High limit

Low limit

External stop

Approx. origin

External comm.

Jog reverse

HOME COM

HOME +5V

38

37

1

MPG A+

2

MPG A-

3

MPG B+

4

MPG B-

5V

A

B

0V

MPG

G4F-PP1/2/3D

OPP of Servo ON signal

Cutoff by alarm signal

DC24V

ENG

8

CON

7

ZONE 1

11

COM

10

ZONE 3

13

ZONE 2

12

ZONE COM

14

Emergency stop

External Simultaneous start

(2) G6F-PP1/2/3D

RD

SD

GND

GND

RS

CS

DR

ER

OPC

11

PP

3

PG

13

NP

2

NG

12

RD

19

COM

9

CR

8

SG

10

LZ

5

LZR

15

LG

1

SD

Plate

EMG

15

SON

5

RES

14

PC

8

TL

9

LSP

16

LSN

17

SG

10

SG

20

VDD

3

COM

13

ALM

18

ZSP

19

TLC

6

P15R

11

TLA

12

LG

1

SD

Plate

CN1E

DRVIN

34A

DRVIN COM

33A

RP-

RP+

24A

21A

FP+

22A

FP-

23A

Within 10m

External EMG

Servo ON

Reset

Proportional control

Torque limit

Normal limit

Reverse limit

*3

*3

failure

zero speed detection

in torque limit

RA1

RA2

RA3

Analog torque limit

+10V/max. current

Power

3phase 200VAC

NF

L1

L2

L3

L11

L21

CTE2

D

P

CN1A

TE11

MR-J2S-A

U

V

W

PE

PE

HC-MF HA-FF

Series motor

U

V

W

E

EMG

24VDC

CN2

B1

B2

SM

electronic brake

detector

2

1

12

TxD

RxD

LG

11

5

15

LG

LG

LG

4

3

14

13

Plate

GND

RS

CS

DR

ER

CN3

A

A

Monitor output

Max. 10mA

10k

10k

Personal

computer

Within 2m

Within 2m

MC

COM

32A

25A

OV-

STOP

OV+

28A

DOG

29A

VTP

30A

ECMD

26A

27A

JOG-

31A

VTP switching

DC24V

High limit

Low limit

External stop

Approx. origin

External comm.

Jog reverse

HOME COM

HOME +5V

36A

37A

1A

MPG A+

2A

MPG A-

3A

MPG B+

4A

MPG B-

5V

A

B

0V

MPG

G6F-PP1/2/3D

OPP of Servo ON signal

Cutoff by alarm signal

DC24V

ENG

8A

CON

7A

COM

10A

Emergency stop

External simultaneous start

3) MR-J2/J2S-□A Connection (Open Collector)

(1) G4F-PP1/2/3O

Within 10m

External EMG

Servo ON

Reset

Proportional control

Torque limit

Normal limit

Reverse limit

*3

*3

failure

zero speed detection

in torque limit

RA1

RA2

RA3

Analog torque limit

+10V/max. current

Power

3phase 200VAC

NF

RD

SD

GND

GND

RS

CS

DR

ER

L1

L2

L3

L11

L21

CTE2

D

P

CN1A

OPC

11

PP

3

PG

13

NP

2

NG

12

RD

19

COM

9

CR

8

SG

10

LZ

5

LZR

15

LG

1

SD

Plate

EMG

15

SON

5

RES

14

PC

8

TL

9

LSP

16

LSN

17

SG

10

SG

20

VDD

3

COM

13

ALM

18

ZSP

19

TLC

6

P15R

11

TLA

12

LG

1

SD

Plate

CN1E

TE11

MR-J2S-A

U

V

W

PE

PE

HC-MF HA-FF

Series motor

U

V

W

E

EMG

24VDC

CN2

B1

B2

SM

electronic brake

detector

2

1

12

TxD

RxD

LG

11

5

15

LG

LG

LG

4

3

14

13

Plate

GND

RS

CS

DR

ER

CN3

A

A

Monitor output

Max. 10mA

10k

10k

Personal

computer

Within 2m

Within 2m

MC

DRVIN

34

DRVIN COM

33

RP-

RP+

24

21

FP+

22

FP-

23

COM

32

25

OV-

STOP

OV+

28

DOG

29

VTP

30

ECMD

26

27

JOG-

31

VTP switching

DC24V

High limit

Low limit

External stop

Approx. origin

External comm.

Jog reverse

HOME COM

HOME +5V

38

37

1

MPG A+

2

MPG A-

3

MPG B+

4

MPG B-

5V

A

B

0V

MPG

G4F-PP1/2/3O

OPP of Servo ON signal

Cutoff by alarm signal

DC24V

ENG

8

CON

7

ZONE 1

11

COM

10

ZONE 3

13

ZONE 2

12

ZONE COM

14

Emergency stop

DC24V

External Simultaneous start

(2) G6F-PP1/2/3O

RD

SD

GND

GND

RS

CS

DR

ER

OPC

11

PP

3

PG

13

NP

2

NG

12

RD

19

COM

9

CR

8

SG

10

LZ

5

LZR

15

LG

1

SD

Plate

EMG

15

SON

5

RES

14

PC

8

TL

9

LSP

16

LSN

17

SG

10

SG

20

VDD

3

COM

13

ALM

18

ZSP

19

TLC

6

P15R

11

TLA

12

LG

1

SD

Plate

CN1E

DRVIN

34A

DRVIN COM

33A

RP-

RP+

24A

21A

FP+

22A

FP-

23A

Within 10m

External EMG

Servo ON

Reset

Proportional control

Torque limit

Normal limit

Reverse limit

*3

*3

failure

zero speed detection

in torque limit

RA1

RA2

RA3

Analog torque limit

+10V/max. current

Power

3phase 200VAC

NF

L1

L2

L3

L11

L21

CTE2

D

P

CN1A

TE11

MR-J2S-A

U

V

W

PE

PE

HC-MF HA-FF

Series motor

U

V

W

E

EMG

24VDC

CN2

B1

B2

SM

electronic brake

detector

2

1

12

TxD

RxD

LG

11

5

15

LG

LG

LG

4

3

14

13

Plate

GND

RS

CS

DR

ER

CN3

A

A

Monitor output

Max. 10mA

10k

10k

Personal

computer

Within 2m

Within 2m

MC

COM

32A

25A

OV-

STOP

OV+

28A

DOG

29A

VTP

30A

ECMD

26A

27A

JOG-

31A

VTP switching

DC24V

High limit

Low limit

External stop

Approx. origin

External comm.

Jog reverse

24V

HOME COM

HOME +5V

36A

38A

P COM

37A

1A

MPG A+

2A

MPG A-

3A

MPG B+

4A

MPG B-

5V

A

B

0V

MPG

G6F-PP1/2/3O

OPP of Servo ON signal

Cutoff by alarm signal

DC24V

ENG

8A

CON

7A

COM

10A

Emergency stop

External simultaneous start

40A

DC24V

4) MR-J□A Connection (Line drive)

R

S

T

R1

S1

N

C

P

U

V

W

U

V

W

E

24

22

21

29

33

30

28

32

15

20

34

35

36

26

1

12

31

19

SON

RES

TL

LSP

LSN

VIN

VDD

CR

SG

PP

PG

NP

NG

RD

P15R

OP

VDD

ZSP

27

ALM

16

SG

P15R

LG

MO

LG

SD

6

4

1

3

18

7

TLA

14

SG

13

SG

DRVIN

33

RP-

RP+

24

21

FP+

22

FP-

23

HOME COM

HOME +5V

38

34

DRVIN COM

37

7

CON

COM

EMG

10

8

ZONE COM

ZONE 3

14

11

ZONE 1

12

ZONE 2

13

COM

32

25

OV-

STOP

OV+

28

DOG

29

VTP

30

ECMD

26

27

JOG-

31

VTP switching

DC24V

High limit

Low limit

External stop

Approx. origin

External comm.

Jog reverse

Servo ON

Reset

Torque limit

Normal limit

Reverse limit

1

MPG A+

2

MPG A-

3

MPG B+

4

MPG B-

5V

A

B

0V

MPG

DC24V

Emergency stop

RA1

RA2

detection

failure

Analog torque limit command(+)

+10V/max. current

Monitor max. +1mA

G4F-PP1/2/3D

Within 10m

Within 2m

power

3상 AC200V

Servo motor

SM

detector

Within 30m

Revival option

MR-JA

CN1

CN1

CN2

option

External simultaneous start   Zero speed

5) MR-C□A Connection (Line drive)

HOME COM

HOME +24V

38

35

9

10

7

8

13

12

1

4

11

17

15

14

2

PP

PG

NP

NG

CR

SG

V+

OP

SD

SON

LSP

LSN

ALM

V24

20

24V power

supply

Within 10m

G4F-PP/1/2/3D

+

-

≥ 24V 0.2A

Power

200VAC(A type) or

100VAC(A1 type)

Revival resistance (Option)

NF

MC

L1

L2

TE1

U

V

W

MR-CA or MR-CA1

CN1

CN2

EMG

24VDC

OPP of Servo ON signal

Cutoff by alarm signal

electronic brake

detector

SM

U

V

W

W

HC-PQ

Series motor

RP-

24

RP+

21

FP+

22

FP-

23

COM

32

25

OV-

STOP

OV+

28

DOG

29

VTP

30

ECMD

26

27

JOG-

31

VTP switching

High limit

Low limit

External stop

Approx. origin

External comm

Jog reverse

DRVIN

34

DRVIN COM

33

1

MPG A+

2

MPG A-

3

MPG B+

4

MPG B-

5V

A

B

0V

MPG

Driver READY

Servo ON

Normal limit

Reverse limit

failure           RA1

DC24V

ENG

8

CON

7

ZONE 1

11

COM

10

ZONE 3

13

ZONE 2

12

ZONE COM

14

Emergency stop

l		Single phase

Single phase

External simultaneous start

6) MINAS A Series Connection (Line drive)

3

4

1

MPG B+

MPG B-

MPG A-

MPG A+

2

PULSE2

PULSE1

SIGN2

SIGN1

OZ-

OZ+

S-RDY+

21

9

22

10

37

23

35

S-RDY-

SRV-QN

CCWL

CWL

COM+

34

29

9

8

7

G4F-PP1/2/3D

Max. 2m

5V

A

B

0V

+5V

5G

MPG

24G

P24V

MINAS A

RP-

24

RP+

21

FP+

22

FP-

23

HOME COM

HOME +5V

38

37

DRVIN

34

DRVIN COM

33

COM

32

25

OV-

STOP

OV+

28

DOG

29

VTP

30

ECMD

26

27

JOG-

31

VTP switching

High limit

Low limit

External stop

Approx. origin

External comm

Jog reverse

DC24V

start

ENG

8

CON

7

ZONE 1

11

COM

10

ZONE 3

13

ZONE 2

12

ZONE COM

14

Emergency stop

External simultaneous

A20

B20

A19

MPG B+

MPG B-

MPG A-

MPG A+

B19

PPC

PPC

CNPC

NPC

5-24VDC

SG

COP

SRDY

26

27

28

29

50

13

11

41

12-24VDC

SG

SG

49

24

25

SON

PROT

37

32

NROT

5-24VDC

33

23

G4F-PP1/2/3D

Max. 2m

5V

A

B

0V

+5V

MPG

5G

24G

P24V

PYO

RP-

24

RP+

21

FP+

22

FP-

23

HOME COM

HOME +24V

38

35

DRVIN

34

DRVIN COM

33

COM

32

25

OV-

STOP

OV+

28

DOG

29

VTP

30

ECMD

26

27

JOG-

31

VTP switching

High limit

Low limit

External stop

Approx. origin

External comm

Jog reverse

DC24V

ENG

8

CON

7

ZONE 1

11

COM

10

ZONE 3

13

ZONE 2

12

ZONE COM

14

Emergency stop

7) PYO Series Connection (Line drive)

External simultaneous start

8) CACR(R Series) Connection (Line drive)

PULS

*PULS

SIGN

*SIGN

PCOT

S-ON

ALM RST

21

9

22

10

37

8

43

N-OT

P-OT

+24VIN

26

41

7

1k

RP-

24

RP+

21

FP+

22

FP-

23

HOME COM

HOME +24V

38

35

DRVIN

34

DRVIN COM

33

P24V

24G

COM

32

25

OV-

STOP

OV+

28

DOG

29

VTP

30

ECMD

26

27

JOG-

31

VTP switching

High limit

Low limit

External stop

Approx. origin

External comm

Jog reverse

1

2

MPG A+

MPG A-

3

4

MPG B+

MPG B-

5V

A

B

0V

MPG

Max. 2m

CACR (R Series)

Servopack

G4F-PP1/2/3D

DC24V

ENG

8

CON

7

ZONE 1

11

COM

10

ZONE 3

13

ZONE 2

12

ZONE COM

14

Emergency stop

External simultaneous start

9) VEXTA UDX2107 Connection

(1) Open Collector

CW-

CW+

CCW-

CCW+

H OFF+

H OFF-

TIMING

COM

O H

P24V

24G

5G

P5V

RP-

24

RP+

21

FP+

22

FP-

23

HOME COM

HOME +24V

38

35

DRVIN

34

DRVIN COM

33

1

2

MPG A+

MPG A-

3

4

MPG B+

MPG B-

5V

A

B

0V

MPG

COM

32

25

OV-

STOP

OV+

28

DOG

29

VTP

30

ECMD

26

27

JOG-

31

VTP switching

High limit

Low limit

External stop

Approx. origin

External comm

Jog reverse

Max. 2m

G4F-PP1/2/3O

VEXTA UDX2107

Connect when required

DC24V

ENG

8

CON

7

ZONE 1

11

COM

10

ZONE 3

13

ZONE 2

12

ZONE COM

14

Emergency stop

External simultaneous start

(2) Line Drive

CW+

CW-

CCW+

CCW-

H OFF+

H OFF-

TIMING

COM

O H

P24V

24G

5G

P5V

RP-

24

RP+

21

FP+

22

FP-

23

HOME COM

HOME +24V

38

35

DRVIN

34

DRVIN COM

33

1

2

MPG A+

MPG A-

3

4

MPG B+

MPG B-

5V

A

B

0V

MPG

COM

32

25

OV-

STOP

OV+

28

DOG

29

VTP

30

ECMD

26

27

JOG-

31

VTP switching

High limit

Low limit

External stop

Approx. origin

External comm

Jog reverse

Max. 2m

G4F-PP1/2/3D

VEXTA UDX2107

Connect when required

DC24V

ENG

8

CON

7

ZONE 1

11

COM

10

ZONE 3

13

ZONE 2

12

ZONE COM

14

Emergency stop

External simultaneous start

10) VEXTA UPD Connection

(1) Open Collector

CW-

CW+

CCW-

CCW+

H OFF+

H OFF-

TIMING

COM

O H

G4F-PP1/2/3O

P24V

24G

P5V

5G

Connect when required

Max. 2m

VEXTA UPO

HOME COM

HOME +24V

38

35

DRVIN

34

DRVIN COM

33

RP-

24

RP+

21

FP+

22

FP-

23

1

MPG A+

2

MPG A-

3

MPG B+

4

MPG B-

5V

A

B

0V

MPG

COM

32

25

OV-

STOP

OV+

28

DOG

29

VTP

30

ECMD

26

27

JOG-

31

VTP switching

High limit

Low limit

External stop

Approx. origin

External comm

Jog reverse

DC24V

ENG

8

CON

7

ZONE 1

11

COM

10

ZONE 3

13

ZONE 2

12

ZONE COM

14

Emergency stop

External simultaneous start

CW-

CW+

CCW-

CCW+

H OFF+

H OFF-

TIMING

COM

O H

G6F-PP1/2/3O

P24V

24G

5G

Connect when required

Max. 2m

VEXTA UPO

HOME COM

HOME +24V

36A

35A

DRVIN

34A

DRVIN COM

33A

RP-

24A

RP+

21A

FP+

22A

FP-

23A

1A

MPG A+

2A

MPG A-

3A

MPG B+

4A

MPG B-

5V

A

B

0V

MPG

COM

32A

25A

OV-

STOP

OV+

28A

DOG

29A

VTP

30A

ECMD

26A

27A

JOG-

31A

VTP switching

High limit

Low limit

External stop

Approx. origin

External comm

Jog reverse

DC24V

ENG

8A

CON

7A

COM

10A

Emergency stop

External simultaneous start

5V

P COM

39A

38A

P5V

(2) Line Drive

CW+

CW-

CCW+

CCW-

H OFF+

H OFF-

TIMING

COM

O H

G4F-PP1/2/3D

P24V

24G

P5V

5G

Connect when required

Max. 10m

VEXTA UPO

HOME COM

HOME +24V

38

35

DRVIN

34

DRVIN COM

33

RP-

24

RP+

21

FP+

22

FP-

23

1

MPG A+

2

MPG A-

3

MPG B+

4

MPG B-

5V

A

B

0V

MPG

COM

32

25

OV-

STOP

OV+

28

DOG

29

VTP

30

ECMD

26

27

JOG-

31

VTP switching

High limit

Low limit

External stop

Approx. origin

External comm

Jog reverse

DC24V

ENG

8

CON

7

ZONE 1

11

COM

10

ZONE 3

13

ZONE 2

12

ZONE COM

14

Emergency stop

External simultaneous start

CW+

CW-

CCW+

CCW-

H OFF+

H OFF-

TIMING

COM

O H

HOME COM

HOME +24V

36A

35A

DRVIN

34A

DRVIN COM

33A

RP-

24A

RP+

21A

FP+

22A

FP-

23A

External simultaneous start

G6F-PP1/2/3D

P24V

24G

P5V

5G

Connect when required

Max. 10m

VEXTA UPO

1A

MPG A+

2A

MPG A-

3A

MPG B+

4A

MPG B-

5V

A

B

0V

MPG

COM

32A

25A

OV-

STOP

OV+

28A

DOG

29A

VTP

30A

ECMD

26A

27A

JOG-

31A

VTP switching

High limit

Low limit

External stop

Approx. origin

External comm

Jog reverse

DC24V

ENG

8A

CON

7A

COM

10A

Emergency stop

11) VEXTA-FX Connection

(1) Open Collector

CW-

CW+

CCW-

CCW+

CL+

CL-

H.OFF+

H.OFF-

ENC A

11

12

9

10

22

21

33

34

15

ENC B

ENC Z

P.END

ALARM

ENC A

13

23

29

25

16

ENC B

14

ENC Z

P.END

ALARM

GND

COMMON

24

30

26

2

1

P24V

24G

P5V

RP-

24

RP+

21

FP+

22

FP-

23

HOME COM

HOME +5V

38

37

DRVIN

34

DRVIN COM

33

1

2

MPG A+

MPG A-

3

4

MPG B+

MPG B-

5V

A

B

0V

MPG

COM

32

25

OV-

STOP

OV+

28

DOG

29

VTP

30

ECMD

26

27

JOG-

31

VTP switching

High limit

Low limit

External stop

Approx. origin

External comm

Jog reverse

5G

G4F-PP1/2/3O

Max. 2m

VEXTA-FX

DC24V

ENG

8

CON

7

ZONE 1

11

COM

10

ZONE 3

13

ZONE 2

12

ZONE COM

14

Emergency stop

External simultaneous start

(2) Line Drive

CW+

CW-

CCW+

CCW-

CL+

CL-

H.OFF+

H.OFF-

ENC A

12

11

10

9

22

21

33

34

15

ENC B

ENC Z

P.END

ALARM

ENC A

13

23

29

25

16

ENC B

14

ENC Z

P.END

ALARM

GND

COMMON

24

30

26

2

1

P24V

24G

P5V

RP-

24

RP+

21

FP+

22

FP-

23

HOME COM

HOME +5V

38

37

DRVIN

34

DRVIN COM

33

1

2

MPG A+

MPG A-

3

4

MPG B+

MPG B-

5V

A

B

0V

MPG

COM

32

25

OV-

STOP

OV+

28

DOG

29

VTP

30

ECMD

26

27

JOG-

31

VTP switching

High limit

Low limit

External stop

Approx. origin

External comm

Jog reverse

5G

G4F-PP1/2/3D

Max. 10m

VEXTA-FX

DC24V

ENG

8

CON

7

ZONE 1

11

COM

10

ZONE 3

13

ZONE 2

12

ZONE COM

14

Emergency stop

External simultaneous start

12) FDA-3000 AC Servo Driver Connection (Open Collector)

PFIN

PRIN

+24VA

PZO+

PZO-

SVON

INPOS

9

26

41

35

36

17

16

0 SPEED

BRAKE

ALARM

A_CODE0

A_CODE1

32

47

48

15

31

A_CODE2

14

GND24

GND24

CCWLIM

49

50

SVONEN

CLR

10

12

30

P24V

24G

RP-

24

RP+

21

FP+

22

FP-

23

HOME COM

HOME +5V

38

37

DRVIN

34

DRVIN COM

33

1

2

MPG A+

MPG A-

3

4

MPG B+

MPG B-

5V

A

B

0V

MPG

COM

32

25

OV-

STOP

OV+

28

DOG

29

VTP

30

ECMD

26

27

JOG-

31

VTP switching

High limit

Low limit

External stop

Approx. origin

External comm

Jog reverse

G4F-PP1/2/3O

Max. 2m

FDA-3000

P24V

24G

CWLIM

46

ESTOP

45

ALMRST

P/P1

13

29

TL

28

+24VIN

+24VIN

27

42

13) FDA-5000 AC Servo Driver Connection (Open Collector)

PFIN

PPFIN

PRIN

PPRIN

PZO+

PZO-

RDY

INPOS

10

11

12

9

5

30

21

22

0 SPEED

BRAKE

ALARM

A_CODE0

A_CODE1

47

48

20

45

19

A_CODE2

44

GND24

GND24

CCWLIM

24

25

SVONEN

CLR

18

38

15

P24V

24G

RP-

24

RP+

21

FP+

22

FP-

23

HOME COM

HOME +5V

38

37

DRVIN

34

DRVIN COM

33

1

2

MPG A+

MPG A-

3

4

MPG B+

MPG B-

5V

A

B

0V

MPG

COM

32

25

OV-

STOP

OV+

28

DOG

29

VTP

30

ECMD

26

27

JOG-

31

VTP switching

High limit

Low limit

External stop

Approx. origin

External comm

Jog reverse

G4F-PP1/2/3O

Max. 2m

FDA-5000

P24V

24G

CWLIM

40

ESTOP

39

ALMRST

P/P1

38

41

TLIM

14

+24VIN

49

1.5K, 1/2W1

1.5K,1/2W

1.5K,1/2W

DC24V

ENG

8

CON

7

ZONE 1

11

COM

10

ZONE 3

13

ZONE 2

12

ZONE COM

14

Emergency stop

External Simultaneous start

14) SGDA-□□□P Connection Example

(1) Open Collector

HOME COM

HOME +5V

38

37

1

2

3

4

5

6

24

25

13

PULS

*PULS

SIGN

*SIGN

CLR

*CLR

PCO

*PCO

+24V

14

16

17

18

S-ON

P-OT

N-OT

ALMRST

SG

19

Within 2m

G4F-PP1/2/3O

power

200VAC(A type) or

100VAC(B type)

NF

MC

R

T

U

V

W

SGDA-BP

1CN

M

U

V

W

E

RP-

24

RP+

21

FP+

22

FP-

23

COM

32

25

OV-

STOP

OV+

28

DOG

29

VTP

30

ECMD

26

27

JOG-

31

VTP switching

Approx. origin

External comm

Jog reverse

DRVIN

34

DRVIN COM

33

1

MPG A+

2

MPG A-

3

MPG B+

4

MPG B-

5V

A

B

0V

MPG

Driver READY

24V power

supply

≥24V 0.2A

Servo ON

Normal limit

Reverse limit

PG

30

31

32

ALO1

ALO2

ALO3

SG-AL

33

20

21

22

PAO

*PAO

PBO

*PBO

23

High limit

Low limit

External stop

7

EMG

CON_STR

10

IN COM

8

External

Alarm reset

+

-

12V

0V

1 KΩ

1 KΩ

Alarm code output

(Open Collector)

Encoder output

DC24V

ENG

8

CON

7

ZONE 1

11

COM

10

ZONE 3

13

ZONE 2

12

ZONE COM

14

Emergency stop

Single phase

Single phase

External simultaneous start

(2) Line Drive

HOME COM

HOME +5V

38

37

1

2

3

4

5

6

24

25

13

PULS

*PULS

SIGN

*SIGN

CLR

*CLR

PCO

*PCO

+24V

14

16

17

18

S-ON

P-OT

N-OT

ALMRST

SG

19

Within 10m

G4F-PP1/2/3D

Power 200VAC(A type) or

100VAC(B type)

NF

MC

R

T

U

V

W

SGDA-BP

1CN

M

U

V

W

E

RP-

24

RP+

21

FP+

22

FP-

23

COM

32

25

OV-

STOP

OV+

28

DOG

29

VTP

30

ECMD

26

27

JOG-

31

VTP switching

Approx. origin

External comm

Jog reverse

DRVIN

34

DRVIN COM

33

1

MPG A+

2

MPG A-

3

MPG B+

4

MPG B-

5V

A

B

0V

MPG

Driver READY

24V power

supply

≥ 24V 0.2A

Servo ON

Normal limit

Reverse limit

PG

30

31

32

ALO1

ALO2

ALO3

SG-AL

33

20

21

22

PAO

*PAO

PBO

*PBO

23

High limit

Low limit

External stop

7

EMG

CON_STR

10

IN COM

8

Emergency stop

Alarm reset

+

-

Alarm code output

(Open Collector)

Encoder output

DC24V

ENG

8

CON

7

ZONE 1

11

COM

10

ZONE 3

13

ZONE 2

12

ZONE COM

14

Emergency stop

Single phase

Single phase

External simultaneous start

.