Chapter 7 Function Block

Here describes Function Block of positioning module for GMWIN.

The types of function block are as follows.

| No. | Classification | Function block name | #### Description | Detailed description | Action condi- tion | Running time |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Module information | CRD | Code Status Read | Operation status code information read | Level | Within 1㎲ |
| 2 |  | SRD | Status Read | Operation status bit information read | Level | Within 1㎲ |
| 3 | Parameter setting | SBP | Set Basic Parameter | Basic parameter setting | Edge | Within 1100ms |
| 4 |  | SEP | Set Extended Parameter | Extended parameter setting | Edge | Within 1100ms |
| 5 |  | SCP | Set Common Parameter | Common parameter setting | Edge | Within 1100ms |
| 6 |  | SHP | Set Homing Parameter | Homing parameter setting | Edge | Within 1100ms |
| 7 |  | SMP | Set Manual Operation Parameter | Manual operation parameter setting | Edge | Within 1100ms |
| 8 | Operation data | SMD | Set Move Data | Operation data setting | Edge | Within 1100ms |
| 9 | Automatic operation | ORG | Return to Origin | Origin return start | Edge | Within 5ms |
| 10 |  | DST | Direct Start | Direct start | Edge | Within 5ms |
| 11 |  | IST | Indirect Start | Indirect start | Edge | Within 5ms |
| 12 |  | LIN | Linear Interpolation Start | Linear interpolation start | Edge | Within 6ms |
| 13 |  | CIN | Circular Interpolation Start | Circular interpolation start | Edge | Within 9ms |
| 14 |  | SST | Simultaneous Start | Simultaneous start | Edge | Within 5ms |
| 15 |  | PST | Point Start | PTP start | Edge | Within 5ms |
| 16 | Manual operation | JOG | Jog Start | Jog start | Level | Within 6ms |
| 17 |  | INC | Inching Start | Inching start | Edge | Within 5ms |
| 18 |  | MPG | Manual Pulse Generator | Manual pulse generator operation (or encoder) | Edge | Within 6ms |
| 19 |  | RTP | Return to Position | Automatic operation position return start | Edge | Within 5ms |
| 20 | Auxiliary operation | SSP | Synchronous Start by Position | Position synchronous start | Edge | Within 5ms |
| 21 |  | SSS | Synchronous Start by Speed | Speed synchronous start | Edge | Within 5ms |
| 22 |  | POR | Position Override | Position override | Edge | Within 5ms |
| 23 |  | SOR | Speed Override | Speed override | Edge | Within 5ms |
| 24 |  | PSO | Position Speed Override | Position speed override | Edge | Within 5ms |
| 25 |  | PTV | Position to Velocity | position/speed control | Edge | Within 5ms |
| 26 |  | VTP | Velocity to Position | Speed/position control | Edge | Within 5ms |
| 27 |  | SKP | Skip | Skip operatin | Edge | Within 9ms |
| 28 |  | NMV | Next Move | Next move | Edge | Within 5ms |
| 29 |  | SNS | Set Next Step Number | Start step no. setting | Edge | Within 5ms |
| 30 |  | SRS | Set Repeat Step Number | Start step no. setting in repeat operation | Edge | Within 5ms |
| 31 |  | STP | Stop | Stop | Edge | Within 5ms |
| 32 | Teaching | TEA | Position/Speed Teaching (single) | Position/speed teaching (ROM, RAM) (Single) | Edge | ROM: within 1100ms RAM: within 6ms |
| 33 |  | ATEA | Position/Speed Teaching (Array) | Position/speed teaching (ROM, RAM) (Array) | Edge | ROM: Within 1100ms RAM: Within 6ms |
| 34 | Error | EMG | Emergency | Emergency stop | Edge | Edge |
| 35 |  | RST | Error Reset / Inhibit Release | Error reset /output inhibit release | Edge | Within 5ms |
| 36 | Others | ZONE | Zone Output Enable | Zone output permitted | Edge | Within 5ms |
| 37 |  | MOF | M Code Off | M code Off | Edge | Within 6ms |
| 38 |  | PRS | Preset | Current position preset | Edge | Within 5ms |
| 39 |  | FLT | Floating Point Set | Floating point setting | Edge | Within 9ms |
| 40 |  | EPRE | Encoder Preset | Encoder preset | Edge | Within 5ms |
| 41 |  | ENCRD | Encoder Read | Encoder read | Level | Within 1㎲ |
| 42 |  | MDRD | Move Data Read | Operation Data Read | Level | Within 1㎲ |

7.1 Positioning Module function block registration at GMWIN

7.1.1 Function block registration procedure

When GMWIN runs, function block is registered according to the following procedure.

Function block registration is available only in the state that project is open.

Project (P)

Select

Library insert (I)

Select

G4F – PP1O

G4F – PP2O

G4F – PP3O

G4F – PP1D

G4F – PP2D

G4F – PP3D

Special.4fb

GM4 Series registration

(GMWIN V3.6 above)

G6F – PP1O

G6F – PP2O

G6F – PP3O

G6F – PP1D

G6F – PP2D

G6F – PP3D

Special.6fb

GM6 Series registration

(GMWIN V3.63 above)

7.1.2 Common Items of Function Block

1)The function and use method of I/O variable name as below is applied commonly to all function block of Article 7.2.

| Classifi cation | Variable name | Data type | Description |
| --- | --- | --- | --- |
| Input | REQ | BOOL | Required area for function block execution ● If the contion connected to this area during program running is formed and “0→1” (riging edge) or level input detection, function block runs. |
|  | BASE | USINT | Base position no. ●This is the area to set the no. of base equiped with positioning module. ● Setting range : 0 ∼ 3 |
|  | SLOT | USINT | Position no. of slot ●This is the area to set the no. of slot equiped with positioning module. ● Setting range : 0 ∼ 7 |
|  | AXIS | USINT | Area to set the use axis ●X axis : 0 ●Y axis : 1 ●Z axis : 2 ● If out of setting range, “error 6” occurs. |
| Output | DONE | BOOL | Indication area of function block completion status ● If function block completed without error, the output is “1” and it is maintained by the next execution, If error occurs, the output is “0”. |
|  | STAT | USINT | Indication area of error status ● This is the area to output the error no. if error occurs during function block execution. |

2) This is applied commonly to all function blocks to be described in Article 7.2 and the setting range of position and speed is shown as below and the position and speed to be described in Article 7.2 ~ 7.10 is based on pulse unit.

| Classification | Setting unit | Setting Range |
| --- | --- | --- |
| Position | pulse | -2,147,483,648 ∼ 2,147,483,647 [puse] |
|  | mm | -2,147,483,648 ∼ 2,147,483,647 [X10-4㎜] |
|  | inch | -2,147,483,648 ∼ 2,147,483,647 [X10-5Inch] |
|  | degree | -2,147,483,648 ∼ 2,147,483,647 [X10-5degree] |
| Speed | pls/s | Open Collector output : 1 ∼ 200,000 [pls/s] Line Drive output : 1 ∼ 1,000,000 [pls/s] |
|  | ㎜/min | 1 ∼ 2,000,000,000[X10-2㎜/min] |
|  | inch/min | 1 ∼ 2,000,000,000[X10-3Inch/min] |
|  | degree/min | 1 ∼ 2,000,000,000[X10-3 degree/min] |

7.2 Module Information Read Function Block

7.2.1 Current Operation Status Code Information Read  (Status Code Read	   APM_CRD)

This carries out the monitoring by reading the current position address, operation speed, operation data no., M code of the setting axis and it can be used as a condition for user’s program.

| Function Block type | Variable | Data type | Description |
| --- | --- | --- | --- |
|  | ERR | UINT | Indicates the error information during operation |
|  | CA | DINT | Indicates the current position Address |
|  | CV | UINT | Indicates the current operation speed |
|  | STEP | UINT | Indicates the current operation data no. |
|  | MCD | USINT | Indicates the current M code |

7.2.2 Current Operation Status Bit Information Read (Status Bit Read	APM_SRD)

The contents of output variable ST1 ∼ ST7 of current operation status Bit read function block is the important information to apply for the Program.

G6F-PP10~30, G6FPP1D~3D does not have Zone 1,2,3 output signal of ST7[3], ST7[4], ST7[5].

| Function block type | Variable | Data type | Description |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Bit no | Execution | Bit no | Execution |
|  | ST1 | BOOL [ARRAY] | [0] | In operation (0: Stop, 1:BUSY) | [4] | Origin setting status (0: No, 1:Yes) |
|  |  |  | [1] | Error status | [5] | Pulse output prohibited status (0: Enable, 1: prohibited) |
|  |  |  | [2] | Positioning completion | [6] | Stop status |
|  |  |  | [3] | M Code On signal (0:Off, 1:On) | [7] | No use |
|  | ST2 | BOOL [ARRAY] | [0] | High limit detection | [4] | Acceleration |
|  |  |  | [1] | Low limit detection | [5] | Constant speed |
|  |  |  | [2] | Emergency stop status | [6] | Deceleration |
|  |  |  | [3] | normal/reverse direction (0: normal, 1:reverse) | [7] | Dwell |
|  | ST3 | BOOL [ARRAY] | [0] | 1axis position control operation | [4] | 2 axis circular interpolation |
|  |  |  | [1] | 1 axis speed control operation | [5] | Origin return operation |
|  |  |  | [2] | 2 axis linear interplation l | [6] | Position synchronous operation |
|  |  |  | [3] | 3 axis linear interpolation | [7] | Speed synchronous operation |
|  | ST4 | BOOL [ARRAY] | [0] | Jog low speed operation | [4] | Manual operation point return |
|  |  |  | [1] | Jog high speed operation | [5] | Zone 1 |
|  |  |  | [2] | Inching operation | [6] | Zone 2 |
|  |  |  | [3] | MPG operation | [7] | Zone 3 |
|  | ST5 | BOOL [ARRAY] | [0] | Axis status (0: subordinate, 1: main) | [4] | Main axis information (Encoder) |
|  |  |  | [1] | Main axis information (X) | [5] | No use |
|  |  |  | [2] | Main axis information (Y) | [6] | No use |
|  |  |  | [3] | Main axis information (Z) | [7] | No use |
|  | ST6 | BOOL [ARRAY] | [0] | Emergency stop input signal | [4] | High limit input signal |
|  |  |  | [1] | Stop input signal | [5] | Low limit input signal |
|  |  |  | [2] | Command input signal | [6] | Origin input signal |
|  |  |  | [3] | Jog high speed reverse signal | [7] | Approximate origin input signal |
|  | ST7 | BOOL [ARRAY] | [0] | speed/position control switching input | [4] | Zone2 output signal |
|  |  |  | [1] | Driver ready input signal | [5] | Zone3 output signal |
|  |  |  | [2] | External synchronous start input | [6] | No use |
|  |  |  | [3] | Zone1 output signal | [7] | No use |

7.3 Parameter Setting Function Block

7.3.1 Basic Parameter Setting  (Set Basic Parameter		APM_SBP)

This is used to change the basic parameter during operation without using S/W Package.

| Function block type | Variable | Data type | Description |
| --- | --- | --- | --- |
|  | MAX_ SPD | UDINT | Speed limit ●Setting range : Open Collector output 0 ∼ 200,000 [unit:pls/s] Line Driver output 0 ∼ 1,000,000 [unit:pls/s] ●If out of setting range, “Error 11” occurs. |
|  | BIAS _SPD | UDINT | Bias speed ●Setting range : Open Collector output 0 ∼ speed limit settinng value [unit:pls/s] Line Driver output 0 ∼ speed limit setting value [unit:pls/s] ●If out of setting range, “Error 11” occurs. |
|  | ACC_ DEC1 | UINT | Acceleration/Deceleration Time No1 ●Setting range : 0 ~ 65,535 [unit:㎳] |
|  | ACC_ DEC2 | UINT | Acceleration/Deceleration Time No2 ●Setting range : 0 ~ 65,535 [unit:㎳] |
|  | ACC_ DEC3 | UINT | Acceleration/Deceleration Time No3 ●Setting range : 0 ~ 65,535 [unit:㎳] |
|  | ACC_ DEC4 | UINT | Acceleration/Deceleration Time No4 ●Setting range : 0 ~ 65,535 [unit:㎳] |
|  | PLS_ NO | UINT | No. of pulse per rotation ●Setting range : 1 ~ 65,535 |
|  | TRAV _VAL | UINT | Travel distance per rotation ●Setting range : Control unit; Setting range; Actual input value; Setting range. Pulse; 1 ~ 65,535; 1 ~ 65,535; pls. ㎜; 0.1 ~ 6,553.5; * 1/10 ㎛. Inch; 0.00001 ~ 0.65535; * 1/10000 inch. Phase; 0.00001 ~ 0.65535; * 1/10000 degree. |
|  | PLS_ MODE | USINT | Pulse output mode ●Setting range : 1 ~ 2 [ 0 : CW/CCW, 1 : Pulse/Dir , 2 : Phase ] ●If out of setting range, “Error 11” occur. |
|  | UNIT | USINT | Control unit ●Setting range : 0 ~ 3 [ 0: Pulse, 1: ㎜, 2: Inch, 3: Degree ] ●If out of setting range, “Error 11 ” occurs. |
|  | UNIT _MAG | USINT | Unit magnification ●Setting range : 0 ~ 3 [ 0 : X 1times, 1 : X 10times, 2 : X 100times, 3 : X 1000times ] ●If out of setting range, “Error 11” occurs. |

| Point |  |
| --- | --- |
| 1) If the setting range is set as “0” when entering acceleration/deceleration time, it disregards the speed set by bias and starts by the setting speed without acceleration/deceleration section. |  |

7.3.2 Extended Parameter Setting (Set Extended Parameter		APM_SEP)

This is used to change the extended parameter during operation without using S/W Package.

| Function block type | Variable | Data type | Description |
| --- | --- | --- | --- |
|  | UP_ LMT | DINT | Soft upper limit ●Setting range : -2,147,483,648 ~ +2,147,483,647 |
|  | LOW_ LMT | DINT | Soft lower limit ●Setting range : -2,147,483,648 ~ +2,147,483,647 |
|  | BACK LASH | UINT | Backlash compensation amount ●Setting range : 0 ~ 65,535 |
|  | POS_ TIME | UINT | Positioning completion signal output time ●Setting range : 0 ~ 65,535 [unit:㎳] |
|  | S_RA TE | USINT | S-Curve rate ●Setting range : 1 ~ 100 [unit:%] ●if out of setting range, “Error 11” occurs. |
|  | ECMD _SEL | USINT | External command signal selection ●Setting range : 0 ~ 2 [ 0: start, 1: JOG operation, 2: Skip operation ] ●if out of setting range, “Error 11 ” occurs. |
|  | PLS_ DIR | BOOL | Pulse output direction ●Setting range : 0 ~ 1 [0 : CW, 1: CCW ] |
|  | PATT ERN | BOOL | Acceleration/Deceleration pattern ●Setting range : 0 ~ 1 [0 : trapezoid, 1: S-Curve ] |
|  | MCD_ MODE | USINT | M Code mode ●Setting range : 0 ~ 2 [ 0 : None, 1 : With , 2 : After ] ●if out of setting range, “Error 11” occurs. |
|  | PMON _EN | BOOL | Position indication during equal speed operation ●Setting range : 0 ~ 1 [ 0: prohibited, 1: permitted ] |
|  | LMT_ EN | BOOL | Soft upper/lower limit detection during equal speed operation ●Setting range : 0 ~ 1 [ 0: prohibited, 1: permitted ] |
|  | EVTP _FN | BOOL | External speed/position switching permitted/prohibited ●Setting range : 0 ~ 1 [ 0: prohibited, 1: permitted ] |
|  | ECMP _EN | BOOL | External command permitted/prohibited ●Setting range : 0 ~ 1 [ 0: prohibited, 1: permitted ] |
|  | ESTP _EN | BOOL | External stop permitted/prohibited ●Setting range : 0 ~ 1 [ 0: prohibited, 1: permitted ] |
|  | ESST _EN | BOOL | External synchronous start permitted/prohibited ●Setting range : 0 ~ 1 [ 0: prohibited, 1: permitted ] |

7.3.3 Common Parameter Setting (Set Common Parameter		APM_SCP)

This is used to change common parameter during operation without using S/W Package.

| Function block type | Variable | Data type | Description |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | OUT_ LEVL | BOOL | Pulse output level ●Setting range : 0 ~ 1 [ 0 : Low Active, 1 : High Active ] |  |  |  |
|  | ENC_ MODE | USINT | Encoder pulse input mode ●Setting range : 0 ~ 6 |  |  |  |
|  |  |  |  | Setting value | Description |  |
|  |  |  |  | 0 | CW/CCW, 1상1체배 |  |
|  |  |  |  | 1 | CW/CCW, 1상2체배 |  |
|  |  |  |  | 2 | Pulse/Dir, 1상1체배 |  |
|  |  |  |  | 3 | Pulse/Dir, 1상2체배 |  |
|  |  |  |  | 4 | Phase A/B, 2상1체배 |  |
|  |  |  |  | 5 | Phase A/B, 2상2체배 |  |
|  |  |  |  | 6 | Phase A/B, 2상4체배 |  |
|  |  |  | ●If out of setting range, “Error 11 ” occurs. |  |  |  |
|  | ENC_ CLR | BOOL | Counter Clear mode by Z phase input ●Setting range : 0 ~ 1 [ 0 : Not Clear, 1 : Clear] |  |  |  |
|  | ENC_ LD | DINT | Encoder Auto Reload ●Setting range : -2,147,483,648 ~ +2,147,483,647 |  |  |  |
|  | ZON1 _SEL | USINT | Zone1 setting axis ●Setting range : 0 ~ 3 [ 0: X, 1: Y, 2: Z, 3: Encoder ] ●If out of setting range, “Error 11” occurs. |  |  |  |
|  | ZON1 _ON | DINT | Zone1 output ON position ●Setting range : -2,147,483,648~ +2,147,483,647 |  |  |  |
|  | ZON1 _OFF | DINT | Zone1 output OFF position ●Setting range : -2,147,483,648 ~ +2,147,483,647 |  |  |  |
|  | ZON2 _SEL | USINT | Zone2 setting axis ●Setting range : 0 ~ 3 [ 0: X, 1: Y, 2: Z, 3: Encoder ] ●If out of setting range, “Error 11” occurs. |  |  |  |
|  | ZON2 _ON | DINT | Zone2 output ON position ●Setting range : -2,147,483,648 ~ +2,147,483,647 |  |  |  |
|  | ZON2 _OFF | DINT | Zone2 output OFF position ●Setting range : -2,147,483,648 ~ +2,147,483,647 |  |  |  |
|  | ZON3 _SEL | USINT | Zone3 setting axis ●Setting range : 0 ~ 3 [ 0: X, 1: Y, 2: Z, 3: Encoder ] ●If out of setting range, “Error 11” occurs. |  |  |  |
|  | ZON3 _ON | DINT | Zone3 output ON position ●Setting range : -2,147,483,648 ~ +2,147,483,647 |  |  |  |
|  | ZON3 _OFF | DINT | Zone3 output OFF position ●Setting range : -2,147,483,648 ~ +2,147,483,647 |  |  |  |
|  | ZON_ MODE | BOOL | Zone output mode ●Setting range : 0 ~ 1 [ 0: individual output, 1: batch output ] ※ If selected batch output, it follows the setting condition of Zone 1. |  |  |  |
|  | CIN_ METD | BOOL | Circular interpolation method setting ●Setting range : 0 ~ 1 [ 0: middle point, 1: center point ] |  |  |  |

7.3.4 Homing Parameter Setting (Set Homing Parameter		APM_SHP)

This is used to change Homing parameter during operation without using S/W Package.

| Function block type | Variable | Data Type | Description |
| --- | --- | --- | --- |
|  | H_AD DR | DINT | Origin address ●Setting range : -2,147,483,648 ~ +2,147,483,647 |
|  | HSPD _H | UDINT | Homing high speed ●Setting range : 1 ~ less than speed limit setting value [unit:pls/s] ●if out of setting range, “Error 11” occurs. |
|  | HSPD _L | UDINT | Homing low speed ●Setting range : 1 ~ less than speed limit setting value [unit:pls/s] ●if out of setting range, “Error 11” occurs. |
|  | H_TI ME | UINT | Homing Acceleration/Deceleratin time ●Setting range : 1 ~ 65,535 [unit:㎳] |
|  | H_DW T | UINT | Homing Dwell time ●Setting range : 0 ~ 50,000[unit:㎳] ●if out of setting range, “Error 11” occurs. |
|  | H_CO MO | DINT | Homing compensation amount ●Setting range : -2,147,483,648 ~ +2,147,483,647 |
|  | H_WT IME | UINT | Homing reset waiting time ●Setting range : 1 ~ 65,535 [unit:㎳] |
|  | H_MO DE | USINT | Homing mode - Setting range : 0 ~ 4 Setting value; Description. 0; Origin detection after approximate origin OFF. 1; Origin detection after deceleration when approximate orign ON. 2; Origin detection by high/low limit and the origin. 3; Origin detection by approximate origin. 4; High speed origin detection. ●If out of setting range, “Error 11” occurs. |
|  | H_DI R | BOOL | Homing direction ●Setting range : 0 ~ 1 [ 0: normal, 1: reverse] |

7.3.5 Manual Operation Parameter Setting (Set Manual Opertion Parameter	   APM_SMP)

This is used to change manual operation parameter without using S/W Package.

| Function block type | Variable | Data type | Description |
| --- | --- | --- | --- |
|  | JOG_ HIGH | UDINT | JOG high speed ●Setting range : 1 ~ less than speed limit [unit:pls/s] ●If out of setting range, “Error 11” occurs. |
|  | JOG_ LOW | UDINT | JOG low speed ●Setting range : 1 ~ less than JOG high speed[unit:pps] ●If out of setting range, “Error 11” occurs. |
|  | JOG_ TIME | UINT | JOG acceleration/deceleration time ●Setting range : 1 ~ 65,535 [unit:㎳] |
|  | INCH _SPD | UINT | Inching speed ●Setting range : 1 ~ 65,535 [unit:pls/s] |

7.4 Move Data Setting Function Block

7.4.1 Move Data Setting (Set Move Data		APM_SMD)

This is used to change Move data without using S/W Package.

| Function block type | Variable | Data type | Description |
| --- | --- | --- | --- |
|  | STEP | UINT | Operation step no. ●Setting range : 1 ~ 400 ●If out of setting range, “Error 11” occurs. |
|  | MOV_ ADDR | DINT | Goal position address ●Setting range : -2,147,483,648 ~ +2,147,483,647 |
|  | CIN_ ADDR | DINT | Aux. Address of circular interpolation ●Setting range : -2,147,483,648 ~ +2,147,483,647 |
|  | MOV_ SPD | UDINT | Operation speed ●Setting range : Open Collector module : 1 ~ 200,000 [unit:pls/s] Line Driver module : 1 ~ 1,0000,000 [unit:pls/s] ●If out of setting range, “Error 11” occurs. |
|  | DWEL L | UINT | Swell ime ●Setting range : 0 ~ 50,000 [unit:㎳] ●If out of setting range, “Error 11” occurs. |
|  | MCD_ NO | UINT | M Code no. ●Setting range : 0 ~ 65,535 |
|  | POS/ SPD | BOOL | Position/Speed control setting ●Setting range : 0 ~ 1 [ 0: position control, 1: speed control ] |
|  | SIN/ RPT | BOOL | Single/Repeat operation setting ●Setting range : 0 ~ 1 [ 0: single, 1: repeat ] |
|  | MOV_ METH | USINT | End/Go-on/Continuous setting ●Setting range : 0 ~ 2 [ 0: End, 1: Go-on, 2 : Continuous ] ●If out of setting range, “Error 11” |
|  | ABS/ INC | BOOL | Absolute/Relative setting ●Setting range : 0 ~ 1 [ 0 : Absolute, 1 : Relative ] |
|  | TIME _SEL | USINT | Acceleration/Deceleration time no. setting ●Setting range : 0 ~ 3 [ 0: Acc./Dece. Time 1, 1: Acc./Dec. Time No. 2, 2: Acc./Dece. time No 3, 3: Acc./Dece. Time No 4 ] ●If out of setting range, “Error 11”. |
|  | CIN_ DIR | BOOL | Circulation interpolation direction setting ●Setting range : 0 ~ 1 [ 0: CW, 1: CCW ] |

7.5 Automatic Operation Function Block

7.5.1 Origin Return Start (Return To Origin	APM_ORG)

| Function block type | Description |
| --- | --- |
|  | Operation command to find the origin of machine by origin return processing method such as direction, compensation amount, high speed and low speed, address and dwell time set from Homing parameter of each axis and if Homing bit information ST1[4] is “ON”, the homing operation of machine will end. |

7.5.2 Direct Start (Direct Start	APM_DST)

This is used to operate directly by setting the goal position address, operation speed, dwell time, M code no, control method, coordinate setting and acceleration/deceleration time no. without operation  data.

| Function block type | Variable | Data type | Description |
| --- | --- | --- | --- |
|  | ADDR | DINT | Goal position address ●Setting range : -2,147,483,648 ~ +2,147,483,647 |
|  | SPEE D | UDINT | Operation speed setting ●Setting range : Open Collector module : 1 ~ 200,000 [unit:pls/s] Line Driver module : 1 ~ 1,0000,000 [unit:pls/s] ●if out of setting range, “Error 11” occurs. |
|  | DWEL L | DINT | Dwell time setting ●Setting range : 0 ~ 50,000 [unit:㎳] ●If out of setting range, “Error 11” occurs. |
|  | MCOD E | UINT | M Code no. setting ●Setting range : 0 ~ 65,535 |
|  | POS/ SPD | BOOL | Position/speed control setting ●Setting range : 0 ~ 1 [ 0: position control, 1: speed control ] |
|  | ABS/ INC | BOOL | Absolute/Relative setting ●Setting range : 0 ~ 1 [ 0: absolute, 1: relative ] |
|  | TIME _SEL | USINT | Acceleration/Deceleration No. setting ●Setting range : 0 ~ 3 [ 0: acc./dec. Time No 1, 1: acc./dec. time No 2, 2: acc./dec. Time No 3, 3: acc./dec. Time No 4 ] ●If out of setting range, “Error 11” occurs. |

7.5.3 Indirect Start  (Indirect Start	APM_IST)

This is used to operate by setting the operation step no. by operation data.

| Function block type | Variable | Data type | Description |
| --- | --- | --- | --- |
|  | STEP | UINT | Operation step no. ●Setting range : 1 ~ 400 ●If out of setting range, “Error 11” occurs. |

7.5.4 Linear Interpolation Start  (Linear Interpolation Start	APM_LIN)

This is the command to carry out the linear interpolation operation at 2 axis or 3 axis positioning module.

| Function block type | Variable | Data Type | Description |
| --- | --- | --- | --- |
|  | LIN_ AXIS | USINT | Interpolation operation axis setting ●Setting range : 1 ~ 7(except 1,2,4) ●If out of setting range, “Error 6” occurs. Axis information; Setting value; Operation axis. Z(Bit2); Y(Bit1); X(Bit0). Off; On; On; 3; X/Y. On; Off; On; 5; X/Z. On; On; Off; 6; Y/Z. On; On; On; 7; X/Y/Z. |
|  | STEP | UINT | Interpolation operation step no. ●Setting range : 1 ~ 400 ●If out of setting range, “Error 11” occurs. |

7.5.5 Circular Interpolation Start  (Cicular Interpolation Start	APM_CIN)

This is the command to carry out circular interpolation operation at 2 axis or 3 axis positioning module.

| Function block type | Variable | Data type | Description |
| --- | --- | --- | --- |
|  | MST_ AXIS | USINT | Main axis setting ●Setting range : 0 ∼ 2 [ 0: X, 1:Y, 2:Z ] ●If out of setting range, “Error 6” occurs. |
|  | SLV_ AXIS | USINT | Subordinate axis setting ●Setting range : 0 ∼ 2 [ 0: X, 1:Y, 2:Z ] ●If out of setting range, “Error 6” occurs. |
|  | STEP | UINT | Operation step no. setting ●Setting range : 1 ~ 400 ●If out of setting range, “Error 11” occurs. |

7.5.6 Simultaneous Start  (Simultaneous Start     APM_SST)

This is the command to start 2 axis or 3 axis operation simultaneously.

| Function block type | Variable | Data type | Description |
| --- | --- | --- | --- |
|  | SST_ AXIS | USINT | Simultaneous start axis setting ●Setting range : 1 ~ 7(except 1,2,4) ●if out of setting range, “Error 6” occurs. Axis information; Setting value; Operation axis. Z(Bit2); Y(Bit1); X(Bit0). Off; On; On; 3; X/Y. On; Off; On; 5; X/Z. On; On; Off; 6; Y/Z. On; On; On; 7; X/Y/Z. |
|  | X_ STEP | UINT | X axis simultaneous start operation step no. setting ●Setting range : 1 ~ 400 ●If out of setting range, “Error 11” occurs. |
|  | Y_ STEP | UINT | Y axis simultaneous start operation step no. setting ●Setting range : 1 ~ 400 ●If out of setting range, “Error 11” occurs. |
|  | Y_ STEP | UINT | Z axis simultaneous start operation step no. setting ●Setting range : 1 ~ 400 ●If out of setting range, “Error 11” occurs. |

7.5.7 PTP Start  (Point Start		APM_PST)

In case of PTP(Point to Point) operation, this command carries out the operation continuously without stop by setting max. 20 operation steps.

| Function block type | Variable | Data type | Description |
| --- | --- | --- | --- |
|  | PST_ CNT | USINT | Operation step no. setting when PTP operation ●Setting range : 0 ~ 19 ●If out of setting range, “Error 6” occurs. |
|  | PST_ VAL | UINT [ARRAY] [0]~[19] | Operation step no. setting when PTP operation ●Setting range : 1 ~ 400 ●If out of setting range, “Error 6” occurs. |

7.6 Manual Operation Function Block

7.6.1 JOG operation  (Jog Start 	APM_JOG)

This function is manual operation for test and is used to confirm the position address for the action of system , wiring checking and teaching and the speed is divided into high speed and low speed. If connection condtion of input variable REQ is “ON”, the pulse is outputted by the setting value and when “OFF”, it stops.

| Function block type | Variable | Data type | Description |
| --- | --- | --- | --- |
|  | JOG_ DIR | BOOL | Rotation direction setting when JOG operation ●Setting range : 0 ∼ 1 [ 0: normal, 1: reverse ] |
|  | LOW/ HIGH | BOOL | JOG speed setting when JOG operation ●Setting range : 0 ∼ 1 [ 0: Jog low speed operation, 1: Jog high speed operation ] |

7.6.2 Inching Operation  (Inching Start	APM_INC)

This is a kind of manual operation which is used when processing the detailed movement as quantitive operation.

| Function block type | Variable | Data type | Description |
| --- | --- | --- | --- |
|  | INC_ VAL | DINT | The desired position amount setting to move by inching operation ●Setting range : -2147483648 ∼ 2147483647 ▶Inching speed is set by origin/manual parameter of extended parameter of S/W Package. |

7.6.3 Manual Pulse Generator Operation  (Manual Pulse Generator	APM_MPG)

In case of operating by using the manual pulse generator installed outside, this command is used to make the positioning module ready to operate.

| Function block type | Variable | Data type | Description |
| --- | --- | --- | --- |
|  | MPG_ EN | BOOL | MPG[manual pulse generator] operation permitted/prohibited setting ●Setting range : 0 ∼ 1 [ 0: prohibited, 1: permitted ] |

7.6.4 Return to the previous position before Manual Operation (Return To Position

APM_RTP)

| Function block type | Description |
| --- | --- |
|  | When the position is changed by manual operation after positioning, this is used to return it to the previous position before manual operation. ▶In this case, manual operation includes inching operation, jog operation, manual pulse generator operation. |

7.7 Auxiliary Operation Function Block

7.7.1 Synchronous Start by Position (Synchronous Start by Position	APM_SSP)

If the axis in operation is the subordinate axis and reaches the goal position set by the main axis, the operation step set here will act.

| Function block type | Variable | Data type | Description |
| --- | --- | --- | --- |
|  | STEP | UINT | Operation step no. setting for synchronous start by the operating axis ●Setting range : 1 ∼ 400 |
|  | MST_ AXIS | USINT | Main axis setting ●Setting range : 0 ∼ 2 [ 0: X, 1:Y, 2:Z ] ●If out of setting range, “Error 6” occurs. |
|  | MST_ ADDR | DINT | Goal position setting of main axis ●Setting range : -2147483648 ∼ 2147483647 |

7.7.2 Synchronous Start by Speed  (Synchronous Start by Speed	APM_SSS)

This is used to control the operation speed between 2 axis by the setting rate.

(speed rate of slave axis / Speed rate of master axis has to be set less than “1”)

| Function block type | Variable | Data type | Description |
| --- | --- | --- | --- |
|  | AXIS | USINT | Subordinate axis setting ●Setting range : 0 ∼ 2 [ 0: X, 1:Y, 2:Z ] ●If out of setting range, “Error 6” occurs |
|  | MSP_ AXIS | USINT | Main axis setting ●Setting range : 0 ∼ 2 [ 0: X, 1:Y, 2:Z ] ●If out of setting range, “Error 6” occurs. |
|  | MST_ RAT | UINT | Main axis Speed rate setting ●Setting range : 0 ∼ 65535 |
|  | SLV_ RAT | UINT | Subordinate axis speed rate setting ●Setting range : 0 ∼ 65535 |

7.7.3 Position Override  (Position Override 	APM_POR)

This is used to change the goal position from operation data of the step no. in operation of each axis.

| Function block type | Variable | Data type | Description |
| --- | --- | --- | --- |
|  | POR_ ADDR | DINT | New goal position setting ●Setting range : -2147483648 ∼ 2147483647 |

7.7.4 Speed Override  (Speed Override	APM_SOR)

This is used to change the operation speed from operation data of step no. in operation of each axis.

| Function block type | Variable | Data type | Description |
| --- | --- | --- | --- |
|  | SOR_ SPD | UDINT | New operation speed setting ●Setting range : Open Collector output 0 ∼ 200,000 [unit:pls/s] Line Driver output 0 ∼ 1,000,000 [unit:pls/s] ●If out of setting range, “Error 11” occurs. |

7.7.5 Position/Speed Override  (Position Speed Override	APM_PSO)

This is used to change the goal position and speed from operation data of step no. in operation of each axis simultaneously.

| Function block type | Variable | Data type | Description |
| --- | --- | --- | --- |
|  | PSO_ ADDR | DINT | New goal position setting ●Setting range : -2147483648 ∼ 2147483647 |
|  | PSO_ SPD | UDINT | New operation speed setting ●Setting range : Open Collector output 0 ∼ 200,000 [unit:pls/s] Line Driver output 0 ∼ 1,000,000 [unit:pls/s] ●If out of setting range, “Erro 11” occurs. |

7.7.6 Position/Velocity Switching Control (Position To Velocity	APM_PTV)

| Function block type | Description |
| --- | --- |
|  | While the axis set as positioning action carries out the position control by the setting transfer amount, it carries out the switching operation from position control to speed control by the position/velocity switching signal. If this command is executed, the origin becomes the unsettled state at the very executed time and carries out the speed control mode action by the setting speed from operation data. |

7.7.7 Velocity/Position Switching Control  (Velocity To Position	APM_VTP)

| Function block type | Description |
| --- | --- |
|  | While the axis set by the positioning action carries out the speed control, it is switched from speed control to position control by the velocity/position switching signal and carries out the positioning as much as by the setting transfer amount. If this command is executed, the origin will be determined at the very executed time and complete the positioning after moving to the setting goal position. |

7.7.8 SKIP Operation  (Skip 	APM_SKP)

| Function block type | Description |
| --- | --- |
|  | This is used to carry out the operation by moving to next step without operating the operation step. Whenever it executes, it operates the next operation step by skipping and stopping the operation of the current operation step. |

7.7.9 Continuous Operation  (Next Move	APM_NMV)

| Function block type | Description |
| --- | --- |
|  | This is used to carry out the operation by moving to next step without operating the operation step. Whenever it executes, it operates the next operation step by skipping and non-stopping the operation of the current operation step. |

7.7.10 Start Step Number Setting  (Set Next Step Number	APM_SNS)

This is used to change the operation step of the setting axis. Indirect start carries out the operation by increasing the operation step one by one after completion of start and changes it with specific operation step.

(In case of the step no = “0”)

| Function block type | Variable | Data type | Description |
| --- | --- | --- | --- |
|  | STEP | UINT | Operation step no. setting for operation ●Setting range : 1 ~ 400 ●If out of setting range, “Error 11” occurs. |

7.7.11 Start Step No. Setting when Repeat operation  (Set Repeat Step Number     APM_SRS)

The setting axis returns always to no.1 operation step when encounters the repeat operation while operating by operation data. But this is used to start the operation from the specific operation step by setting the start step no. when repeat operation.

| Function block type | variable | Data type | Description |
| --- | --- | --- | --- |
|  | STEP | UINT | Operation step no. setting for repeat operation ●Setting range : 1 ~ 400 ●If out of setting range, “Error 11” occurs. |

7.7.12 Stop  (Stop 	APM_STP)

| Function block type | Description |
| --- | --- |
|  | This is used to stop the positioning module in operation. If encounters the stop command during the operation by operation data, it carries out the deceleration stop and then starts to operate again by Start command. The availalble operation are 1) indirect start, 2) direct start, 3) inching, 4) interpolation operation. |

7.8 Teaching Function Block

7.8.1 Position/Speed Teaching Function Block_Single (Teaching	APM_TEA)

Speed teaching is used when the user wants to use the random speed for the specific operation data no. while Position teaching is used when the use wants to set the random address to the specific operation step no.

| Function block type | Variable | Data type | Description |
| --- | --- | --- | --- |
|  | STEP | UINT | Operation step no. setting for teaching ●Setting range : 1 ~ 400 ●If out of setting range, “Error 11” occurs. |
|  | RAM/ ROM | BOOL | Selection of RAM teaching and ROM teaching ●Setting range : 0 ~ 1 [ 0 : RAM teaching, 1 : ROM teaching] |
|  | POS/ SPD | BOOL | Selection of Position teaching and Speed teaching ●Setting range : 0 ~ 1 [ 0 : Position teaching, 1 : Speed teaching] |
|  | TEA_ VAL | DINT | Teaching value setting ●Position teaching range : -2147483648 ∼ 2147483647 ●Setting range : Open Collector output 1 ∼ 200,000 [unit:pls/s] Line Driver output 1 ∼ 1,000,000 [unit:pls/s] ●If out of setting range, “Error 11” occurs. |

7.8.2 Position/Speed Teaching Function Block _Plural (Array Teaching	APM_ATEA)

This is used to change the goal position and speed by max. 16 at one time by plural teaching function block.

| Function block type | Variable | Data type | Description |
| --- | --- | --- | --- |
|  | STEP | UINT | Operation step no. setting for array teaching ●Seting range : 1 ~ 400 ●If out of setting range, “Error 11” occurs. |
|  | RAM/ ROM | BOOL | Selection of RAM teaching and ROM teaching ●Setting range : 0 ~ 1 [ 0 : RAM teaching, 1 : ROM teaching] |
|  | POS/ SPD | BOOL | Selection of Position teaching and Speed teaching ●Setting range : 0 ~ 1 [ 0 : Position teaching, 1 : Speed teaching] |
|  | TEA/ CNT | USINT | Teaching number setting ●Setting range : 1 ~ 16 ●Max. Teaching no. is 16. ●If out of setting range, “Error 11” occurs. |
|  | TEA_ VAL | DINT [Array] [0]~[15] | Teaching value setting ●Position teaching range : -2147483648 ∼ 2147483647 ●Speed teaching setting range : Open Collector output 0 ∼ 200,000 [unit:pls/s] Line Driver output 0 ∼ 1,000,000 [unit:pls/s] ●If out of setting range, “Error 11” occurs. ●Teaching value is valid as much as the constant number set by TEA/CNT. |

7.9 Error Function Block

7.9.1 Emergency Stop  (Emergency	APM_EMG)

| Function block type | Description |
| --- | --- |
|  | This is used to stop the operation in case of emergent status. All axis where this command is executed becomes stop status. As this is in converted to the status of output prohibited and origin unsettled, it is required to release the output prohibited and determine the origin again before reset. |

7.9.2 Error Reset/Output Prohibit Release  (Error Reset/Inhibit Release	APM_RST)

This is used to release the status that the pulse output is prohibited by external emergency stop, high/low limit detection or reset the error when the setting range of parameter is excessive or the error occurs during operation.

| Function block type | Variable | Data type | Description |
| --- | --- | --- | --- |
|  | INH_ OFF | BOOL | Error reset or output prohibit release ●Setting range : 0 ~ 1 [ 0 : error reset, 1 : error reset/output permit] |

7.10 Other Function Block

7.10.1 Zone Output Permit  (Zone Output Enable	APM_ZONE)

This is the command to permit the output to internal / external Zone output by using the position data of the axis in operation and the position data value set by Zone1, Zone2, Zone3 for the zone set by common parameter of S/W Package.(but the GM6 APM module has the internal Zone output)

| Function block type | Variable | Data type | Description |
| --- | --- | --- | --- |
|  | ZONE _EN | BOOL | The internal Zone output/external Zonr output(Tr) permitt/prohibit setting ●Setting range : 0 ~ 1 [ 0 : output prohibit, 1 : output permit] ●The output status can be confirmed through Out1 ~ Out3. |

7.10.2 M Code Off  (M Code Off	 APM_MOF)

| Function block type | Description |
| --- | --- |
|  | In case that M code is set as With or After mode from parameter of each axis, this is used to make M code signal “OFF” when it is “ON”. |

7.10.3 Preset  (Preset		APM_PRS)

This is the command to change the current position with random position and if it is executed, the origin will be determined again.

| Function block type | Variable | Data type | Description |
| --- | --- | --- | --- |
|  | PRS_ ADDR | DINT | ● Preset Setting range : -2147483648 ∼ 2147483647 |

7.10.4 Floating Origin  (Floating Point Set	APM_FLT)

| Function block type | Description |
| --- | --- |
|  | This is the command to force to set the current position as the origin without carrying out the origin return action of machine and the setting address of origin return addres shall be the current position. |

7.10.5 Encoder Preset  (Encoder Preset	      APM_EPRE)

| Function block type | Variable | Data type | Description |
| --- | --- | --- | --- |
|  | EPRE_ VAL | UDINT | ● Encoder preset setting range : 0 ∼ 4,294,967,295 |

7.10.6 Encoder Read   (Encoder Read	    APM_ENCRD)

| Function block type | Variable | Data Type | Description |
| --- | --- | --- | --- |
|  | ENC_ VAL | UDINT | ● Encoder Read : 0 ∼ 4,294,967,295 |

7.10.7 Operation Data Read   (Move Data Read	APM_MDRD)

| Function block type | Variable | Data Type | Description |
| --- | --- | --- | --- |
|  | STEP | UINT | Operation step no. setting for operation data read ● setting range : 1 ~ 400 ● If out of setting range, “Error 11” occurs. |
|  | ADDR | DINT | ● Teaching Positon Read : -2,147,483,648 ~ 2,147,483,647 |
|  | SPD | UDINT | ● Teaching Speed Read : Open Collector : 1 ~ 200,000 [unit:pls/s] Line Drive : 1 ~ 1,0000,000 [unit:pls/s] |

7.11 Function Block Error Code

Here describes the error types that are shown on output variable STAT and its solutions.

| Error code | # Error description | Output type |  | Module action | Solution |
| --- | --- | --- | --- | --- | --- |
|  |  | ## Open | Line |  |  |
| 0 | Normal action | O |  | Normal |  |
| 1 | Position no. of Base exceeds the setting range. | O |  | Stop | Adjust the base position within the setting range |
| 2 | H/W error of the corresponding base | O |  | Stop | Ask the A/S for the base |
| 3 | Position no. of slot exceeds the setting range. | O |  | Stop | Adjust the slot position within the setting range. |
| 4 | The corresponding slot not installed | O |  | Stop | Install Positioning module to the corresponding slot. |
| 5 | The module name of the corresponding slot is different. | O |  | Stop | Install positioning module to the corresponding slot. |
| 6 | The setting axis no. exceeds the setting range. | O |  | Stop | Set the axis no. of positioning module correctly. |
| 8 | Common RAM error | O |  | H/W error occur | A/S asking |
| 9 | Function block command impossible as the module is in operation/stop | O |  | Error occur | Set the command condition correctly. |
| 10 | New command function block is executed before completing the previous command. | O |  | Error occur | Program change to execute new command after completing the previous command |
| 11 | The setting aux. Input value exceeds the setting range. | O |  | Stop | Adjust within the setting range. |
| 13 | During function block execution, the stop related command or emrgency stop is entered. | O |  | Error occur | - Error initialization - Output prohibit Release |

Here describes the error types and its solution that are shown on output variable ERR of APM_CRD function block.

The more than Error code 101 is used to the GM4/GM6 and MASTER-K200S/300S.

| Error code | # Error description | Output type |  | Module action | Solution |
| --- | --- | --- | --- | --- | --- |
|  |  | ## Open | Line |  |  |
| 101 | Exceeds the range without acc./dec. Time of basic parameter | O |  | Stop | Asjust acc./dec.time within the setting range 0~ 65535. |
| 101 | Max. Speed of basic parameter exceeds the range. | O |  | Stop | Max.speed of basic parameter is more than 1 and less than 200000 for OpenCollector and more than 1 and less than 1000000 for Line Driver based on pulse unit. |
| 102 | Bias speed of basic parameter exceeds the range. | O |  | Stop | Bias speed of basic parameter should be smaller than max. Speed of basic parameter. |
| 103 | Pulse output mode of basic parameter exceeds the range. | O |  | Stop | Pulse output mode of basic parameter is 0:CW/CCW 1:Pulse/Dir 2:Phase A/B. Select one from these three modes. |
| 111 | Soft upper/lower limit of extended parameter exceeds the range. | O |  | Stop | S/W upper limit of extended parameter should be greater than or equal to S/W lower limit of extended parameter. |
| 112 | M code mode of extended parameter exceeds the range | O |  | Stop | M code output of extended parameter is 0:None 1:With 2:After. Select one from these three modes. |
| 113 | S-curve rate of extended parameter exceeds the range. | O |  | Stop | Modify the S-curve rate of extended parameter to be more than 1 and less than 100. |
| 114 | External command selection of extended parameter exceeds the range. | O |  | Stop | External command selection of extended parameter is 0:start 1:JOG command 2:SKIP. Select one from these three. |
| 121 | Jog high speed of manual operation parameter exceeds the range. | O |  | Stop | Set Jog high speed of manual operation parameter within the range greater or equal to bias speed of basic parameter and within the range smaller or equal to max. Speed of basic parameter. |
| 122 | Jog low speed of manual operation parameter exceeds the range. | O |  | Stop | Set Jog low speed of manual operation parameter within the range more than 1 and less than Jog high speed of manual operation parameter. |
| 123 | Inching speed of manual operation parameter exceeds the range. | O |  | Stop | Set the inching speed of manual operation parameter within the range greater than or equal to bias speed of manual operation parameter and within the rage smaller or equal to max. Speed of basic parameter. |
| 131 | Homing mode of homing parameter exceeds the range. | O |  | Stop | Homing method of homing parameter is 0:Dog/origin(Off) 1:Dog/origin(On) 2:high/low limit/origin 3:approximate origin 4: high speed origin. Select one from these. |
| 132 | Homing address of homing parameter exceeds the range. | O |  | Stop | Set the homing address of homing parameter as the value greater than S/W lower limit of extended parameter and smaller than S/W upper limit of extended parameter. |
| 133 | Homing high speed of homing parameter exceeds the range. | O |  | Stop | Set the homing high speed of homing parameter within the Range greater than or equal to bias speed of basic parameter and within the range smaller than or equal to max. Speed of basic parameter. |
| 134 | Homing low speed of homing parameter exceeds the range. | O |  | Stop | Set the homing low speed of homing parameter within the range greater than or equal to bias speed of basic parameter and within the range smaller or equal to homing high speed of homing parameter. |
| 135 | Homing dwell time of homing parameter exceeds the range. | O |  | Stop | Set the Dwell time of homing parameter as less than 50000. |
| 141 | Encoder Type of common parameter exceeds the range. | O |  | Stop | Set the encoder input signal of common parameter between 0 ~ 6.. |
| 142 | Zone1 axis setting value of common parameter exceeds the range. | O |  | Stop | Zone1 axis setting of common parameter is 0:X 1:Y 2:Z 3: Encoder. Select one from these. |
| 143 | Zone2 axis setting value of common parameter exceeds the range. | O |  | Stop | Zone2 axis setting of common parameter is 0:X 1:Y 2:Z 3: Encoder. Select one from these. |
| 144 | Zone3 axis setting value of common parameter exceeds the range. | O |  | Stop | Zone3 axis setting of common parameter is 0:X 1:Y 2:Z 3: Encoder. Select one from these. |
| 145 | Pulse output level setting of common parameter exceeds the range. | O |  | Stop | Pulse output level of common parameter is 0:Low Active 1:High Active. Select one from these. |
| 146 | Zone output mode setting of common parameter exceeds the range. | O |  | Stop | Zone output mode of common parameter is 0: individual output 1:batch output (Zone1). Select one from these. |
| 147 | Circular interpolation method of common parameter exceeds the range. | O |  | Stop | Circular interpolation method of common parameter is 0: middle point 1: center point. Select one from these. |
| 151 | Operation speed of operation data can not be set as “0”. | O |  | Stop | Set the operation speed as the value greater than “0”. |
| 152 | Operation speed of operation data exceeds max. Speed. | O |  | Stop | Set the operation speed as the value smaller than or equal to max. Speed of basic parameter. |
| 153 | Operation speed of operation data is set as less than bias speed. | O |  | Stop | Set the operation speed as the value greater than or equal to bias speed of basic parameter. |
| 154 | Dwell time of operation data exceeds the range. | O |  | Stop | Set the Dwell time to operate as less than 50000. |

| Error code | # Error description | Output type |  | Module action | Solution |
| --- | --- | --- | --- | --- | --- |
|  |  | ## Open | Line |  |  |
| 155 | End/Go-on/Continuous operation of operation data exceed the range. | O |  | Stop | Set operation pattern of operation data by selecting one from 0:End 1:Go-on 2: Continuous. |
| 201 | Homing command can not be used in operation status. | O |  | Move | Check if the command axis is in operation or not when giving the homing command. |
| 202 | Homing command can not be used in output prohibit satus. | O |  | Stop | Checkif the command axis is in output prohibit status or not when giving the homing command. Output prohibit is released by RST command as output prohibit release option. |
| 203 | Homing command can not be used in SERVO Ready OFF | O |  | Stop | Check if Driver ready signal of command axis is “OFF” when giving the homing command. |
| 211 | Floating origin command can not be used in opertion satus. | O |  | Move | Check if the command axis is in operation when giving the floating point setting command.. |
| 212 | Floating origin command can not be used in SERVO Ready OFF. | O |  | Stop | Check if Driver ready signal of command axis is OFF when giving the floating point setting command. |
| 221 | Direct start command can not be used in operation status. | O |  | Move | Check if the command axis is in operation when giving direct start command. |
| 222 | Direct start command can not be used in output prohibit status. | O |  | Stop | Check if the command axis is in output prohibit status when giving direct start command. Output prohibit is released by RST command as output prohibit release option. |
| 223 | Direct start command can not be used in M Code ON. | O |  | Stop | Checkif M code signal of command axis is ON when giving direct start command. M code shall be OFF by MOF command. |
| 224 | Direct start command can not be used in the absolute coordinate of origin unsettled status. | O |  | Stop | Not available to carry out Absolute coordinate operation in origin unsettled status. Check the coordinate of operation data to operate and the current origin determination status. After setting the origin by homing command or floating point setting command, it is available to carry out the Absolute coordinate operation. |
| 225 | Direct start command can not be used in SERVO Ready OFF. | O |  | Stop | Check if Driver ready signal of command axis is OFF when giving direct start command. |
| 231 | Indirect start command can not be used in operation status. | O |  | Move | Check if the command axis is in operation status when giving indirect start command. |
| 232 | Indirect start command can not be used in output prohibit status. | O |  | Stop | Check if the command axis is in output prohibit status when giving indirect start command. Output prohibit shall be released by RST command as output prohibit release option. |
| 233 | Indirect start command can not be used in M Code ON. | O |  | Stop | Check if M code signal of command axis is ON when giving indirect start command. M code shall be OFF by MOF command. |
| 234 | Indirect start command can not be used in the absolute coordinate of origin unsettled status. | O |  | Stop | Not available to carry out Absolute coordinate operation in origin unsettled status. Check the step coordinate to operate and the current origin determination status. After setting the origin by homing command or floating point setting command, it is available to carry out the Absolute coordinate operation |
| 235 | Indirect start command can not be used in SERVO Ready OFF. | O |  | Stop | Check if Driver ready signal of command axis is OFF when giving indirect start command. |
| 236 | Continuous operation of indirect start can not be used with speed control. | O |  | Stop | Check if the control method is set as speed control during Continuous operationof position control from operation data and there is the step set by Continuous operation as operation pattern. |
| 237 | The step no. of Point control is not permitted to exceed 20. | O |  | Stop | Set the step no. to carry out Point control less than 20. |
| 238 | Continuous operation of indirect start can not be carried out for S-Curve Acceleration/Deceleration pattern. | 0 |  | Stop | Check if the acceleration/deceleration pattern of extended parameter of command axis is S-Curve. |
| 241 | Linear interpolation start can not be used in case that the main axis of linear interpolation is in operation. | O |  | Move | Check if the main axis is in operation status when giving linear interpolation command. |
| 242 | Linear interpolation start can not be used in case that the subordinate axis 1 of linear interpolation is in operation. | O |  | Move | Check if the subordinate axis 1 is in operation status when giving linear interpolation command. |
| 243 | Linear interpolation start can not be used in case that the subordinate axis 2 of linear interpolation is in operation. | O |  | Move | Check if the subordinate axis 2 is in operation status when giving linear interpolation command. |
| 244 | Linear interpolation start can not be used in case that the main axis of linear interpolation is in output prohibit status. | O |  | Stop | Check if the main axis is in output prohibit status when giving linear interpolation command. Output prohibit shall be released by RST command as output prohibit release option. |

| Error code | # Error description | Output type |  | Module action | solutions |
| --- | --- | --- | --- | --- | --- |
|  |  | ## Open | Line |  |  |
| 245 | Not available to carry out the linear interpolation start when Linear interpolatin subordinate axis 1 is in output prohibit status. | O |  | Stop | Check if subordinate axis 1 is in output prohibit status when giving linear interpolation command. Output prohibit shall be released by RST command as output prohibit release option. |
| 246 | Not available to carry out the linear interpolation start when Linear interpolation subordinate axis 2 is in output prohibit status. | O |  | Stop | Check if subordinate axis 2 is in output prohibit status when giving linear interpolation command. Output prohibit shall be released by RST command as output prohibit release option. |
| 247 | Not available to carry the linear interpolation start when M code signal of linear interpolation main axis is “ON”. | O |  | Stop | Check if M code signal of main axis is “ON” when giving linear interpolation command. M code shall OFF by MOF command. |
| 248 | Not available to carry the linear interpolation start when M code signal of linear interpolation subordinate axis 2 is “ON”. | O |  | Stop | Check if M code signal of subordinate axis 1 is “ON” when giving linear interpolation command. M code shall OFF by MOF command. |
| 249 | Not available to carry the linear interpolation start when M code signal of linear interpolation subordinate axis 3 is “ON”. | O |  | Stop | Check if M code signal of subordinate axis 2 is “ON” when giving linear interpolation command. M code shall OFF by MOF command. |
| 250 | Not available to carry out the absolute coordinate positioning operation when linear interpolatin main axis is in origin unsettled status. | O |  | Stop | Not available to carry out Absolute coordinate operation in origin unsettled status. Check the step coordinate to operate and the current origin determination status. After setting the origin by homing command or floating point setting command, it is available to carry out the Absolute coordinate operation. |
| 251 | Not available to carry out the absolute coordinate positioning operation when linear interpolatin subordinate axis 1 is in origin unsettled status. | O |  | Stop | Not available to carry out Absolute coordinate operation in origin unsettled status. Check the step coordinate to operate and the current origin determination status. After setting the origin by homing command or floating point setting command, it is available to carry out the Absolute coordinate operation |
| 252 | Not available to carry out the absolute coordinate positioning operation when linear interpolatin subordinate axis 2 is in origin unsettled status. | O |  | Stop | Not available to carry out Absolute coordinate operation in origin unsettled status. Check the step coordinate to operate and the current origin determination status. After setting the origin by homing command or floating point setting command, it is available to carry out the Absolute coordinate operation. |
| 253 | In case that the main axis and subordinate axis of linear interpolation is set wrong (the subordinate axis is not set or only one axis is set or the axis is not set). | O |  | Stop | Check if there is the case that subordinate axis is not set or only one axis is set or the axis or the axis is not set when giving linear interpolation command. |
| 254 | Not available to carry out the operation as SERVO ready is OFF at the linear interpolation main axis. | O |  | Stop | Check if Driver ready signal of main axis is OFF when giving linear interpolation command. |
| 255 | Not available to carry out the operation as SERVO ready is OFF at the linear interpolation subordinate axis 1. | O |  | Stop | Check if Driver ready signal of subordinate axis 1 is OFF when giving linear interpolation command. |
| 256 | Not available to carry out the operation as SERVO ready is OFF at the linear interpolation subordinate axis 2. | O |  | Stop | Check if Driver ready signal of subordinate axis 2 is OFF when giving linear interpolation command. |
| 257 | Not available to carry out the linear interpolation in case that there is no goal position of the main axis. | O |  | Stop | Check if the goal position of operation data of linear interpolation step to carry out the linear interpolation is same as the current position in case of absolute coordinate and it is set as “0” in case of relative orrdinate. |
| 258 | Not available to carry out the linear interpolation when the main axis is speed control. | O |  | Stop | Check if the control method of main axis operation data step to carry out the linear interpolation operation is set as speed control. |
| 259 | Not available to carry out the linear interpolation when the subordinate axis 1 is speed control. | O |  | Stop | Check if the control method of subordinate axis 1 operation data step to carry out the linear interpolation operation is set as speed control. |
| 260 | Not available to carry out the linear interpolation when the subordinate axis 2 is speed control. | O |  | Stop | Check if the control method of subordinate axis 2 operation data step to carry out the linear interpolation operation is set as speed control. |
| 271 | Not available to carry out the circular interpolation start when the circular interpolation main axis is in operation. | O |  | Move | Check if the main axis is operation status when giving circular interpolation command. |
| 272 | Not available to carry out the circular interpolation start when circular interpolation subordinate axis is in operatiob. | O |  | Move | Check if the subordinate axis is operation status when giving circular interpolation command. |
| 273 | Not available to carry out the circular interpolation start when circular interpolation main asix is in output prohibit status. | O |  | Stop | Check if the main axis is in output prohibit status when giving circular interpolation command. Output prohibit shall be released by RST command as output prohibit release option.. |

| Error code | # Error description | Output type |  | Module action | Solutions |
| --- | --- | --- | --- | --- | --- |
|  |  | ## Open | Line |  |  |
| 274 | Not available to carry out circular interpolation start when circular interpolation subordinate axis is in output prohibit status. | O |  | Stop | Check if the subordinate axis is in output prohibit status when giving the circular interpolation command. Output prohibit shall be released by RST command as output prohibit release option. |
| 275 | Not available to carry out circular interpolation start when M code signal of circular interpolation main axis is ON. | O |  | Stop | Check if M code signal of main axis is ON when giving the circular interpolation command. M code shall be OFF by MOF command. |
| 276 | Not available to carry out circular interpolation start when M code signal of circular interpolation subordinate axis is ON. | O |  | Stop | Check if M code signal of subordinate axis is ON when giving the circular interpolation command. M code shall be OFF by MOF command.. |
| 277 | Not available to carry out absolute coordinate positioning operation when circular interpolation main axis is in origin unsettled status. | O |  | Stop | Not available to carry out Absolute coordinate operation in origin unsettled status. Check the step coordinate to operate and the current origin determination status. After setting the origin by homing command or floating point setting command, it is available to carry out the Absolute coordinate operation.. |
| 278 | Not available to carry out absolute coordinate positioning operation when circular interpolation subordinate axis is in origin unsettled status. | O |  | Stop | Not available to carry out Absolute coordinate operation in origin unsettled status. Check the step coordinate to operate and the current origin determination status. After setting the origin by homing command or floating point setting command, it is available to carry out the Absolute coordinate operation. |
| 279 | Not available to carry out the operation as the main axis and subordinate axis is set as equally during circular interpolation. | O |  | Stop | Check the setting of main axis and subordinate axis of circular interpolation command. |
| 280 | Not available to carry out the operation as SERVO ready is OFF at the circular interpolation main axis. | O |  | Stop | Check if Driver ready signal of main axis is OFF when giving circular interpolation command. |
| 281 | Not available to carry out the operation as SERVO ready is OFF at the circular interpolation subordinate axis. | O |  | Stop | Check if Driver ready signal of subordinate axis is OFF when giving circular interpolation command. |
| 282/283 | Not available to carry out Degree operation in the circular interpolation. | O |  | Stop | Check if the unit of basic parameter of circular interpolation command main axis is set as Degree. |
| 284 | Not available to carry out the operatin if start point = center point (middle point) or center point(middle point) = End point in the circular interpolation. | O |  | Stop | Check if center point or middle point is set as the same position of starting point or ending point in the circular interpolation. |
| 285 | The start point is not equal with end point in the middle point method of the circular interpolation. | O |  | Stop | Check if the circular interpolation method of common parameter is set by middle point and the starting point is same as the ending point. |
| 286 | Radius setting error in the circular interpolation. | O |  | Stop | The radius of circle available to carry out the circular interpolation operation is upto 2e31 pulse. Check if it is available to carry out the circular interpolation by the radius greater than that size. |
| 287 | Not available to carry out the operation as the linear profile comes from circular interpolation. | O |  | Stop | Check if the circular interpolation method of common parameter is set by middle point and the middle point is set by linear array with starting point and ending point. |
| 288 | The radius of circular interpolation should be greater than Backlash. | O |  | Stop | The radius of circle to carry out the circular interpolation operation should be greater than Backlash compensation amount set in the extended parameter of main axis and subordinate axis. Check the setting value. |
| 291 | Not available to carry out the synchronous start command in the operation status. | O |  | Move | Check if the axis that error occurred is included in the synchronous start command and there is the axis in operation when giving the synchronous start comand. |
| 292 | Not available to carry out the synchronous start command in the output prohibit status. | O |  | Stop | Check if the axis that error occurred is included in the synchronous start command and it is in output prohibit status when giving the synchronous start command. Output prohibit shall be released by RST command as output prohibit release option. |
| 293 | Not available to carry out the synchronous start command in M code ON status. | O |  | Stop | Check if the axis that error occurred is included in the synchronous start command and M Code signal is ON when giving the synchronous start command. M code shall be OFF by MOFcommand. |
| 294 | Not available to carry out the synchronous start command in case that there is no goal position. | O |  | Stop | Check if the axis that error occurred is included in the synchronous start command and the goal position of operation data step to operate is the same as the current position in case of Absolute coordinate and it is set as “0” in case of Relative coordinate. |
| 295 | Not available to carry out the synchronous start command in SERVO ready when SERVO ready is OFF. | O |  | Stop | Check if the axis that error occurred is included in the synchronous start command and Driver ready signal is OFF when giving the synchronous start command. |

| Error code | # Error description | Output type |  | Module action | Solutions |
| --- | --- | --- | --- | --- | --- |
|  |  | ## Open | Line |  |  |
| 296 | The axis setting of synchronous start command is wrong. | O |  | Stop | Check if the axis setting of synchronous start command is set by one axis. The axis setting address means no.0 bit: X, no.1 bit: Y, no.2bit: Z and each bit is set as “1”. |
| 301 | Not available to carry out speed/position control switching command not in operation status. | O |  | Stop | Check if the axis is in stop status when giving speed/position control switching command. |
| 302 | Not available to carry out speed/position control switching command not in the speed control status. | O |  | Stop | Check if the axis is in speed control status when giving speed/position control switching command. |
| 303 | Not available to carry out speed/position control switching command in the subordinate axis of synchronous operation. | O |  | Stop | Check if the axis is in operation status to the subordinate axis of synchronous operation when giving speed/position control switching command. |
| 304 | Not available to carry out speed/position control switching command in case that there is no goal position. | O |  | Stop | Check if the operation has the position amount when giving speed/position control switching command. |
| 311 | Not available to carry out speed/position control switching command not in the operation status. | O |  | Stop | Check if the axis is in stop status when giving speed/position control switching command |
| 312 | Not available to carry out speed/position control switching command in the subordinate axis of synchronous operation. | O |  | Stop | Check if the axis is in operation status to the subordinate axis of synchronous operation when giving speed/position control switching command. |
| 313 | Not available to carry out speed/position control switching command in the circular interpolation operation. | O |  | Stop | Check if the axis is in circular interpolation operation when giving speed/position control switching command. |
| 314 | Not available to carry out speed/position control switching command in the linear interpolation operation. | O |  | Move | Check if the axis is in linear interpolation operation when giving speed/position control switching command. |
| 321 | Not available to carry out deceleration stop command not in the operation status. | O |  | Stop | Not available to carry out deceleration stop command not In the operation status. |
| 322 | Not available to carry out deceleration stop command in Jog operation status. | O |  | Move | Not available to carry out deceleration stop command in Jog operation status. |
| 323 | Not available to carry out deceleration stop command in the axis of manual pulse generator operation. | O |  | Move | Check if the axis is in manual pulse generator operation when giving deceleration stop command. |
| 331 | Not available to carry out Skip command not in the operation status. | O |  | Stop | Check if the axis is in stop status when giving Skip command. |
| 332 | Not available to carry out Skip command in the axis of linear interpolation operation. | O |  | Move | Check if the axis is in operation to the linear interpolation subordinate axis when giving Skip command. |
| 333 | Not available to carry out Skip command in the subordinate axis of synchronous operation. | O |  | Move | Check if the axis is in operation to the synchronous operation subordinate axis when giving Skip command. |
| 334 | Not available to carry out Skip command in the axis of manual pulse generator operation. | O |  | Move | Check if the axis is in manual pulse generator operation status when giving Skip command Skip. |
| 335 | Not available to carry out Skip command in the Jog operation status. | O |  | Move | Check if the axis is in jog operation status when giving Skip command. |
| 336 | Not available to carry out Skip command in the direct start operation status. | O |  | Move | Check if the axis is in direct start operation status when giving Skip command. |
| 337 | Not available to carry out Skip command in the inching operation status. | O |  | Move | Check if the axis is in inching operation status when giving Skip command. |
| 338 | Not available to carry out Skip command in the subordinate axis of circular interpolation operation. | O |  | Move | Check if the axis is in operation to the circular interpolation subordinate axis when giving Skip command. |
| 341 | Not available to carry position synchronous start command in the operation status. | O |  | Move | Check if the axis is in operation status when giving position synchronous start command. |
| 342 | Not available to carry position synchronous start command in the output prohibit status. | O |  | Stop | Check if the axis is in output prohibit status when giving position synchronous start command. Output prohibit shall be released by RST command as output prohibit release option. |
| 343 | Not available to carry position synchronous start command in the M code “ON” status. | O |  | Stop | Check if the M code signal of the axis is ON when giving position synchronous start command. M code shall be OFF by MOF command. |
| 344 | Not available to carry position synchronous start command in the absolute coordinate of origin unsettled status. | O |  | Stop | Not available to carry out Absolute coordinate operation in origin unsettled status. Check the step coordinate to operate and the current origin determination status. After setting the origin by homing command or floating point setting command, it is available to carry out the Absolute coordinate operation. |
| 345 | Not available to carry position synchronous start command in the SERVO ready OFF status. | O |  | Stop | Check if Driver ready signal of the axis is OFF when giving the synchronous start command. |
| 346 | Not available to carry out position synchronous start command in the origin unsettled status of main axis. | O |  | Stop | Checi if the main axis is in the origin unsettled status when giving position synchronous start command. |
| 347 | Error in setting the main axis and subordinate axis of position synchronous start command. | O |  | Stop | Check if the main axis of position synchronous start command is set as same as the command axis. The main axis is set by the setting address 0 (X),1(Y),2(Z). |

| Error code | # Error description | Output type |  | Module action | solutions |
| --- | --- | --- | --- | --- | --- |
|  |  | ## Open | Line |  |  |
| 348 | Not available to carry out position synchronous start command in the speed control of the main axis with no position indication. | O |  | Stop | Check if the main axis is set as “no indication” from position indication during equal speed operation of extended parameter when giving position synchronous start command and carried out speed control operation. |
| 351 | Not available to carry out speed synchronous start command in operation status. | O |  | Move | Check if the axis is in the operation status(busy) when giving speed synchronous start command. |
| 352 | Not available to carry out speed synchronous start command in output prohibit status. | O |  | Stop | Check if the axis is in the output prohibit status when giving speed synchronous start command. Output prohibit shall be released by RST command as output prohibit release option. |
| 353 | Not available to carry out speed synchronous start command in M Code ON status. | O |  | Stop | Check if M code of he axis is ON when giving speed synchronous start command. M code shall be OFF by MOF command. |
| 354 | Not available to carry out speed synchronous start command in SERVO ready OFF. | O |  | Stop | Check if Driver ready signal of the axis is OFF when giving speed synchronous start command. |
| 355 | Error in setting the main axis/subordinate axis of speed synchronous start command. | O |  | Stop | Check if the main axis of speed synchronous start command is set as same as the command axis. The main axis is set by the setting address 0(X),1(Y),2(Z). |
| 356 | Error in setting the main axis/subordinate axis rate of speed synchronous start command. | O |  | Stop | The main axis rate of speed synchronous start command should be greater than or equal to the subordinate axis rate. check the main axis ratio/subordinate axis ratio setting. |
| 357 | Not available to carry out speed synchronous start command in the specific pulse mode. | O |  | Stop | The speed synchronous start command may not be carried out according to the pulse output mode set by basic parameter of the main axis and the combination of pulse output mode set by basic parameter of the subordinate axis. |
| 361 | Not available to carry out position override command not in the operation status (busy). | O |  | Stop | Check if the axis is in stop status when giving the position override command. |
| 362 | Not available to carry out position override command in dwell status. | O |  | Stop | Check if the axis is in dwell status when giving the position override command. |
| 363 | Not available to carry out position override command not in the positioning operation status. | O |  | Move | Check if the axis is in position control operation status when giving the position override command. |
| 364 | Not available to carry out position override command in the axis of linear interpolation operation. | O |  | Move | Check if the axis is in linear interpolation operation status when giving the position override command. |
| 365 | Not available to carry out position override command in the axis of circular interpolation operation. | O |  | Move | Check if the axis is in circular interpolation operation status when giving the position override command. |
| 366 | Not available to carry out position override command in the subordinate axis of synchronous start opeation. | O |  | Move | Check if the axis is in operation status to the subordinate axis of synchronous start operation when giving the position override command. |
| 367 | Not available to carry out position override command in the axis of manual pulse generator operation. | O |  | Move | Check if the axis is in manual pulse generator operation when giving the position override command. |
| 371 | Not available to carry out speed override command not in the operation status (Busy). | O |  | Stop | Check if the axis is in stop status when giving the speed override command. |
| 372 | Speed override exceeds the range. | O |  | Stop | The speed of speed override command should be smaller than or equal to max. Speed set by basic parameter. Check the speed value. |
| 373 | Not available to carry out speed override command in the subordinate axis of linear interpolation operation. | O |  | Move | Check if the axis is in operation to the linear interpolation subordinate axis when giving the speed override command. |
| 374 | Not available to carry out speed override command in the axis of circular interpolation operation. | O |  | Move | Check if the axis is in operation to the circular interpolation subordinate axis when giving the speed override command. |
| 375 | Not available to carry out speed override command in the subordinate axis of synchronous start operation. | O |  | Move | Check if the axis is in operation to the synchronous start operation subordinate axis when giving the speed override command. |
| 376 | Not available to carry out speed override command in the axis of manual pulse generator operation. | O |  | Move | Check if the axis is in manual pulse generator operation when giving the speed override command. |
| 377 | Not available to carry out speed override command in the deceleration section. | O |  | Move | Check if the axis is in the deceleration stop status when giving speed override command. |
| 378 | Not available to carry out speed override command in the acceleration/deceleration pattern. | O |  | Move | Check if acceleration/deceleration pattern of extended parameter of command axis is S-Curve. |
| 381 | Not available to carry out random position speed override command not in the operation status(busy). | O |  | Stop | Check if the axis is in stop status when giving the random position speed override command. |
| 382 | Not available to carry out random position speed override command not in the positioning operation. | O |  | Stop | Check if the axis is in speed control operation when giving the random position speed override command. |
| 383 | The speed override value of random position exceeds the range of speed override command. | O |  | Stop | The speed of random position speed override commandshould be smaller than or equal to max. speed set by basic parameter. Check the speed. |
| 384 | Not available to carry out random position speed override command in the subordinate axis of linear interpolation operation. | O |  | Move | Check if the axis is in operation to the subordinate axis of linear interpolation when giving the random position speed override command. |

| Error code | # Error description | Output type |  | Module action | solutions |
| --- | --- | --- | --- | --- | --- |
|  |  | ## Open | Line |  |  |
| 385 | Not available to carry out random position speed override command in the axis of circular interpolation operation. | O |  | Move | Check if the axis is in circular interpolation operation when giving the random position speed override command. |
| 386 | Not available to carry out random position speed override command in the subordinate axis of synchronous start operation. | O |  | Move | Check if the axis is in operation to the subordinate axis of synchronous start operation when giving the random position speed override command. |
| 387 | Not available to carry out random position speed override command in the axis of manual pulse generator operation. | O |  | Move | Check if the axis is in manual pulse generator operation when giving the random position speed override command. |
| 388 | Not available to carry out random position speed override command in the SERVO ready OFF. | O |  | Stop | Check if Driver ready signal of the axis is OFF when giving the random position speed override command. |
| 389 | Not available to carry out random position speed override command in the S-curve acceleration/deceleration pattern | O |  | Stop | Check if acceleration/deceleration pattern of extended parameter of command axis is S-Curve. |
| 390 | Not available to carry out Continuous operation command in the S-curve acceleration/deceleration pattern. | O |  | Stop | Check if acceleration/deceleration pattern of extended parameter of command axis is S-Curve. |
| 391 | Not available to carry out Continuous operation command not in the operation status. | O |  | Stop | Check if the axis is in stop status when giving Continuous operation command. |
| 392 | Not available to carry out Continuous operation command not in the dwell status. | O |  | Stop | Check if the axis is in dwell when giving Continuous operation command. |
| 393 | Not available to carry out Continuous operation command not in the positioning operation status. | O |  | Stop | Check if the axis is in speed control operation when giving continuous operation command. |
| 394 | Speed data of Continuous operation command exceeds the allowable range. | O |  | Stop | The speed of next step should be smaller than or equal to max. speed set by basic parameter or more than 0 when giving Continuous operation command. Check the speed. |
| 395 | Not available to carry out Continuous operation command in the subordinate axis of linear interpolation operation. | O |  | Stop | Check if the axis is in operation to the subordinate axis of linear interpolation when giving Continuous operation command. |
| 396 | Not available to carry out Continuous operation command in the axis of circular interpolation operation. | O |  | Stop | Check if the axis is in circular interpolation operation when giving Continuous operation command. |
| 397 | Not available to carry out Continuous operation command in the subordinate axis of synchronous start operation. | O |  | Move | Check if the axis is in operation to the subordinate axis of synchronous start operation when giving Continuous operation command. |
| 398 | Not available to carry out Continuous operation command in the axis of manual pulse generator operation. | O |  | Move | Check if the axis is in manual pulse generator operation when giving Continuous operation command. |
| 399 | Not available to carry out Continuous operation command in the last step of operation data. | O |  | Move | Check if the axis is in operation of 400th step when giving continuous operation command. |
| 400 | Not available to carry out Continuous operation command in the direct start operation. | O |  | Move | Check if the axis is in operation by direct start command when giving Continuous operation command |
| 401 | Not available to carry out Inching command in the operation status. | O |  | Move | Check if the axis is in operation when giving inching command. |
| 402 | Not available to carry out Inching command in the output prohibit status. | O |  | Stop | Check if the axis is in output prohibit status when giving inching command. Output prohibit shall be released by RST command as output prohibit release option. |
| 403 | Not available to carry out Indirect start command in the SERVO ready OFF status. | O |  | Stop | Check if Driver ready signal of the axis is OFF when giving inching command. |
| 411 | Not available to carry out Jog command in the operation status. | O |  | Move | Check if the axis is in operation when giving Jog start command. |
| 412 | Not available to carry out Jog command in the output prohibit status. | O |  | Stop | Check if the axis is in output prohibit status when giving Jog start command. Output prohibit shall be released by RST command as output prohibit release option. |
| 413 | Not available to carry out Jog start command when SERVOready OFF. | O |  | Stop | Check if Driver ready signal of the axis is OFF when giving Jog start command. |
| 421 | Not available to carry out manual pulse generator operationin operation status. | O |  | Move | Check if the axis is in operation when giving manual pulse generator operation command. |
| 422 | Not available to carry out manual pulse generator operation in output prohibit status. | O |  | Stop | Check if the axis is in output prohibit status when giving manual pulse generator operation command. Output prohibit shall be released by RST command as output prohibit release option. |
| 423 | Not available to carry out manual pulse generator operation when SERVO rady OFF. | O |  | Stop | Check if Driver signal of the axis is OFF when giving manual pulse generator operation command. |
| 424 | Not available to carry out manual pulse generator operation in the setting pulse mode. | O |  | Move | Manual pulse generator operation command may not be carried out according to encoder input signal set by common parameter and the combination of pulse output mode set by basic parameter of command axis. |
| 431 | Not available to carry out automatic operation point return command in operation status. | O |  | Move | Check if the axis is in operation when giving automatic operation point return command. |
| 432 | Not available to carry out automatic operation point return command in output prohibit status. | O |  | Stop | Check if the axis is in output prohibit status when giving automatic operation point return command. Output prohibit shall be released by RST command as output prohibit release option. |
| 433 | Not available to carry out indirect start command when SERVO ready OFF. | O |  | Stop | Check if Driver ready signal of the axis is OFF when giving automatic operation point return command |

| Error code | # Error description | Output type |  | Module action | Solutions |
| --- | --- | --- | --- | --- | --- |
|  |  | ## Open | Line |  |  |
| 441 | Not available to carry out start step no. change/repeat operation start step no. setting command in operation status. | O |  | Move | Check if the axis is in operation when giving start step no. change command. |
| 442 | The step of start ste no. change/repeat operation start step no. setting command exceeds the setting range. | O |  | Stop | Check if the setting step no. of start step no. change command or repeat operation start step no. setting command is in the range greater than or equalto 1 and smaller than or equal to 400. |
| 451 | Not available to carry out the current position preset command in operation status. | O |  | Move | Check if the axis is in operation when giving the current position preset command. |
| 452 | The aux. Position data is not allowed to exceed Soft upper/lower limit when giving the current position preset command. | O |  | Stop | Check if the position of the current position preset command is in the range of Soft upper/lower limit set by extended parameter. |
| 461 | Not available to carry out position teaching command in operation status. | O |  | Move | Check if the axis is in operation when giving position teaching command. |
| 462 | Not available to carry out teaching array command for the data over 16. | O |  | - | Check if the data no. of teaching array command is setin the range greater than or equal to 1 and smaller than or equal to 16. |
| 463 | Not available to carry out speed teaching command in operation status. | O |  | Move | Check if the axis is in operation when giving speed teaching command. |
| 464 | The speed of speed teaching command exceeds the setting range. | O |  | Stop | Check if the speed data of speed teaching command is set as greater than 1000000. |
| 465 | Error in setting step no. to carry out teaching command. | O |  | Stop | Check if the step to carry out teaching command is greater than or equal to 1 and smaller than or equal to 400. |
| 471 | Not available to carry out parameter teaching command in operation status. | O |  | Stop | Check if the axis is in operation when giving parameter teaching command. |
| 472 | Not available to carry out operation data teaching command in operation status. | O |  | Move | Check if the axis is in operation when giving operation data teaching command. |
| 481 | Internal emergency stop error | O |  | Stop | Clear the error by removing emergency stop cause and carrying out RST command. Output prohbit shall be released by RST command as output prohbit release option. |
| 491 | External emergency stop error | O |  | Stop | Clear the error by removing emergency stop cause and carrying out RST command. Output prohbit shall be released by RST command as output prohbit release option. |
| 492 | H/w upper limit error | O |  | Stop | Get rid of the external upper limit signal range by Jog command and then carry out RST command and clear the error. Output prohibit shall be released by RST command as output prohibit release option. |
| 493 | H/W lower limit error | O |  | Stop | Get rid of the external lower limit signal range by Jog command and then carry out RST command and clear the error. Output prohibit shall be released by RST command as output prohibit release option. |
| 494 | SERVO driver operation is not available. | O |  | Stop | Check if Driver ready signal is entered correctly. You can check it by external I/O signal window in the monitoring of Software Package and also by reading no.1 bit of SRD function block ST7 or no.9 bit of external I/O signal address. |
| 495 | The position of Upper/lower limit detection Sensor has been changed. | O |  | Stop | Install the upper limit detection sensor in the direction that the current position increases and the lower limit detection sensor in the direction that the current position decreases. |
| 501 | S/W upper limit error | O |  | Stop | Get rid of S/W upper limit signal range by Jog command and then carry out RST command and clear the error. Output prohibit shall be released by RST command as output prohibit release option. |
| 502 | S/W lower limit error | O |  | Stop | Get rid of S/W lower limit signal range by Jog command and then carry out RST command and clear the error. Output prohibit shall be released by RST command as output prohibit release option. |
| 511 | Command code no. is not the reserved no. (only for MASTER-K) | O |  | Stop | Command code is reserved from 1 ~ 38. |
| 512 | Aux. Data step no. exceeds the allowable range. | O |  | Stop | The step greater than 400 was set to the command. Please re-set the step no. within the range from 1 ~ 400. |

*1: Error code 495 is deleted in more than O/S V2.1.